## Main Data
Default Storage Ring Refill Time |  |  | 0.25 | [16 empty] | Refill Timing in Days | 0.010417
Downtime for Run 2018-3
Fill # | Start | End | Length | Loss Reason | DIN # | Audit | Start | End | User Length | System Length | Cause | System | Group | Type | Description | Store Lost | Intention. Dump | Inhibits Beam | TOTAL
1 | 2018-10-02 08:00 | 2018-10-03 06:13 | 22.2167 | Under investigation | 106888 |  | 2018-10-03 06:13 | 2018-10-03 06:47 | 0.56667 | 0.56667 | UNK | UNK | UNK | Store Lost |  | 1 |  |  | 1
2 | 2018-10-03 06:47 | 2018-10-03 12:15 | 5.4667 | S38 RF Cav Vac [RF] | 106889 |  | 2018-10-03 12:15 | 2018-10-03 14:50 | 2.5833 | 2.5833 | RF | RF | RF | Store Lost |  | 1 |  |  | 1
3 | 2018-10-03 14:50 | 2018-10-03 18:54 | 4.0667 | S38 RF Cav Vac [RF] | 106890 |  | 2018-10-03 18:54 | 2018-10-03 20:39 | 1.75 | 1.75 | RF | RF | RF | Store Lost |  | 1 |  |  | 1
4 | 2018-10-03 20:39 | 2018-10-04 08:55 | 12.2667 | RF4 SCR H2O flt [RF] | 106891 |  | 2018-10-04 08:55 | 2018-10-04 10:03 | 1.1333 | 1.1333 | RF | RF | RF | Store Lost |  | 1 |  |  | 1
5 | 2018-10-04 10:03 | 2018-10-07 11:35 | 73.5333 | S38 RF Cav Vac [RF] | 106894 |  | 2018-10-07 11:35 | 2018-10-07 13:29 | 1.9 | 1.9 | RF | RF | RF | Store Lost |  | 1 |  |  | 1
6 | 2018-10-07 13:29 | 2018-10-08 08:00 | 18.5167 | Int Dump: End of Period |  |  |  |  | 0 | 0 |  |  |  | Scheduled |  |  | 1 |  | 1
|  |  | 136.0667 | [5 empty] | 7.9333 | 7.9333 | [8 empty] | 0
7 | 2018-10-09 08:00 | 2018-10-10 05:05 | 21.0833 | S33A:Q2 PS flt [PS] | 106898 |  | 2018-10-10 05:05 | 2018-10-10 07:25 | 2.3333 | 2.3333 | PS | PS | PS | Store Lost |  | 1 |  |  | 1
8 | 2018-10-10 07:25 | 2018-10-12 08:52 | 49.45 | PW pump 30B glitch [MOM] | 106900 |  | 2018-10-12 08:52 | 2018-10-12 10:04 | 1.2 | 1.2 | MOM | MOM | MOM | Store Lost |  | 1 |  |  | 1
9 | 2018-10-12 10:04 | 2018-10-13 05:49 | 19.75 | Adj P0 feedback [AOP] | 106901 |  | 2018-10-13 05:49 | 2018-10-13 05:53 | 0.066667 | 0.066667 | AOP | AOP | AOP | Store Lost |  | 1 |  |  | 1
10 | 2018-10-13 05:53 | 2018-10-15 08:00 | 50.1167 | Int Dump: End of Period |  |  |  |  | 0 | 0 |  |  |  | Scheduled |  |  | 1 |  | 1
|  |  | 140.4 | [5 empty] | 3.6 | 3.6 | [8 empty] | 0
11 | 2018-10-16 08:00 | 2018-10-22 08:00 | 144 | Int Dump: End of Period |  |  |  |  | 0 | 0 |  |  |  | Scheduled |  |  | 1 |  | 1
|  |  | 144 | [5 empty] | 0 | 0 | [8 empty] | 0
12 | 2018-10-23 08:00 | 2018-10-26 17:35 | 81.5833 | Failed bunch removal [AOP] | 106910 |  | 2018-10-26 17:35 | 2018-10-26 18:06 | 0.51667 | 0.51667 | AOP | AOP | AOP | Store Lost |  | 1 |  |  | 1
13 | 2018-10-26 18:06 | 2018-10-29 08:00 | 61.9 | Int Dump: End of Period |  |  |  |  | 0 | 0 |  |  |  | Scheduled |  |  | 1 |  | 1
|  |  | 143.4833 | [5 empty] | 0.51667 | 0.51667 | [8 empty] | 0
14 | 2018-10-31 08:00 | 2018-11-05 08:00 | 121 | Int Dump: End of Period |  |  |  |  | 0 | 0 |  |  |  | Scheduled |  |  | 1 |  | 1
|  |  | 121 | [5 empty] | 0 | 0 | [8 empty] | 0
15 | 2018-11-06 08:00 | 2018-11-09 16:21 | 80.35 | S13B:Q5 trip [PS] | 106915 |  | 2018-11-09 16:21 | 2018-11-09 19:03 | 2.7 | 2.7 | PS | PS | PS | Store Lost |  | 1 |  |  | 1
16 | 2018-11-09 19:03 | 2018-11-11 01:04 | 30.0167 | RF-4 power monitor trip [RF] | 106917 |  | 2018-11-11 01:04 | 2018-11-11 05:10 | 4.1 | 4.1 | RF | RF | RF | Store Lost |  | 1 |  |  | 1
17 | 2018-11-11 05:10 | 2018-11-12 08:00 | 26.8333 | Int Dump: End of Period |  |  |  |  | 0 | 0 |  |  |  | Scheduled |  |  | 1 |  | 1
|  |  | 137.2 | [5 empty] | 6.8 | 6.8 | [8 empty] | 0
18 | 2018-11-13 08:00 | 2018-11-21 08:00 | 192 | Int Dump: End of Period |  |  |  |  | 0 | 0 |  |  |  | Scheduled |  |  | 1 |  | 1
|  |  | 192 | [5 empty] | 0 | 0 | [8 empty] | 0
19 | 2018-11-23 08:00 | 2018-11-25 22:53 | 62.8833 | Power Event [OTH] | 106924 |  | 2018-11-25 22:53 | 2018-11-25 23:26 | 0.55 | 0.55 | ComEd | ComEd | ComEd | Store Lost |  | 1 |  |  | 1
20 | 2018-11-25 23:26 | 2018-11-28 23:42 | 72.2667 | BPLD trip [UNK] | 106928 |  | 2018-11-28 23:42 | 2018-11-29 00:14 | 0.53333 | 0.53333 | UNK | UNK | UNK | Store Lost |  | 1 |  |  | 1
21 | 2018-11-29 00:14 | 2018-12-03 08:00 | 103.7667 | Int Dump: End of Period |  |  |  |  | 0 | 0 |  |  |  | Scheduled |  |  | 1 |  | 1
|  |  | 238.9167 | [5 empty] | 1.0833 | 1.0833 | [8 empty] | 0
|  |  | 0 |  | 106933 |  | 2018-12-04 08:00 | 2018-12-04 10:04 | 2.0667 | 2.0667 | MOM | MOM | MOM | Inhibits beam to user | Water flow fault S39/40 |  |  | 1 | 1
23 | 2018-12-04 10:04 | 2018-12-07 16:19 | 78.25 | 33ID EPS trip [SI] | 106934 |  | 2018-12-07 16:19 | 2018-12-07 17:02 | 0.71667 | 0.71667 | SI | SI | SI | Store Lost |  | 1 |  |  | 1
24 | 2018-12-07 17:02 | 2018-12-10 08:00 | 62.9667 | Int Dump: End of Period |  |  |  |  | 0 | 0 |  |  |  | Scheduled |  |  | 1 |  | 1
|  |  | 141.2167 | [5 empty] | 2.7833 | 2.7833 | [8 empty] | 0
|  |  | 0 |  | 106940 |  | 2018-12-11 08:00 | 2018-12-11 11:07 | 3.1167 | 3.1167 | RF | RF | RF | Inhibits beam to user |  |  |  | 1 | 1
25 | 2018-12-11 11:07 | 2018-12-11 13:26 | 2.3167 | S38, C2 vacuum [RF] | 106941 |  | 2018-12-11 13:26 | 2018-12-11 18:42 | 5.2667 | 5.2667 | RF | RF | RF | Store Lost |  | 1 |  |  | 1
27 | 2018-12-11 18:42 | 2018-12-13 02:27 | 31.75 | S11B:Q3 PS I=0 [PS] | 106943 |  | 2018-12-13 02:27 | 2018-12-13 05:59 | 3.5333 | 3.5333 | PS | PS | PS | Store Lost |  | 1 |  |  | 1
28 | 2018-12-13 05:59 | 2018-12-17 08:00 | 98.0167 | Int Dump: End of Period |  |  |  |  | 0 | 0 |  |  |  | Scheduled |  |  | 1 |  | 1
|  |  | 132.0833 | [5 empty] | 11.9167 | 11.9167 | [8 empty] | 0
|  | Number of Lost Fills | 16 | [5 empty] | Downtime
|  | Number of Intentional Dumps | 10 | [5 empty] | User | System
|  | Number of Fills | 26 | [5 empty] | 34.6333 | 34.6333 | [5 empty] | 16 | 10 | 2 | 28
[16 empty] | SL | Scheduled | Inhibits
|  | Total User Beam | 1526.3667 | 63.5986 | User Beam days
|  | Total User Downtime | 34.6333 | <-- This downtime includes Gaps Open
|  | Total Schedule Run Length | 1561 | [12 empty] | #REF!
26
|  | Mean Time Between Faults | 95.3979
|  | Faults/Day of Delivered Beam | 0.25158 | [13 empty] | #N/A
|  | X-ray Availability | 97.78% | [13 empty] | #N/A
2

## Stats
Group
Data | PS | RF | AOP | SI | ComEd | MOM | UNK | Grand Total
Sum - Inhibits Beam | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 2
Sum - Store Lost | 3 | 6 | 2 | 1 | 1 | 1 | 2 | 16
Sum of System Length | 8.5667 | 19.85 | 0.58333 | 0.71667 | 0.55 | 3.2667 | 1.1 | 34.6333
| RF | Diag | PS | Controls | Accelerator Intlks | Radiation Intlks | Water/ME | Operations | Physics | ID-FE | Electrical-APS | Electrical-ANL | Cooling-ANL | Other | Network | Unidentified | Grand Total | Total Hours
Run 2018-3 | 1.272% |  | 0.5488% |  | 0.04591% |  | 0.2093% | 0.03737% |  |  |  | 0.03523% |  |  |  | 0.07047% | 2.219%
Budget | 0.54% | 0.12% | 0.54% | 0.3% | 0.28% | 0.28% | 0.36% | 0.12% | 0% | 0.06% | 0.06% | 0.06% | 0.06% | 0.18% | 0.12% | 0.06% | 3.14%
Hours for Run | 19.85 |  | 8.5667 |  | 0.71667 |  | 3.2667 | 0.58333 |  |  |  | 0.55 |  |  |  | 1.1 | 34.6333
Faults | 6 |  | 3 |  | 1 |  | 1 | 2 |  |  |  | 1 |  |  |  | 2 | 16
| RF | Diag | PS | Controls | Accelerator Intlks | Radiation Intlks | MOM | Operations | Physics | ID-FE | Electrical-APS | Electrical-ANL | Cooling-ANL | Other | Network | Unidentified
Run 2018-3 | 0.094342 | 0 | 0.047171 | 0 | 0.015724 | 0 | 0.015724 | 0.031447 | 0 | 0 | 0 | 0.015724 | 0 | 0 | 0 | 0.031447 | 0.25158
Budget | 0.12 | 0.03 | 0.12 | 0.05 | 0.035 | 0.02 | 0.06 | 0.02 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.02 | 0.01 | 0.02 | 0.545
Total User Beam | 1526.3667
Total Schedule Run Length | 1561
Filter
Cause
Type | Data | PS | RF | SI | MOM | UNK | ComEd | AOP | Grand Total
Store Lost | Sum - Store Lost | 3 | 6 | 1 | 1 | 2 | 1 | 2 | 16
| Sum - Inhibits Beam | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inhibits beam to user | Sum - Store Lost |  | 0 |  | 0 |  |  |  | 0
| Sum - Inhibits Beam |  | 1 |  | 1 |  |  |  | 2
Total Sum - Store Lost |  | 3 | 6 | 1 | 1 | 2 | 1 | 2 | 16
Total Sum - Inhibits Beam |  | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 2