## Main Data
Default Storage Ring Refill Time |  |  | 0.25 | [16 empty] | Refill Timing in Days | 0.010417
Downtime for Run 2021-3
Fill # | Start | End | Length | Loss Reason | DIN # | Audit | Start | End | User Length | System Length | Cause | System | Group | Type | Description | Store Lost | Intention. Dump | Inhibits Beam | TOTAL
1 | 2021-10-04 08:00 | 2021-10-09 12:40 | 124.6667 | RF4 HVPS trip [RF] |  |  | 2021-10-09 12:40 | 2021-10-09 13:47 | 1.1167 | 1.1167 | RF | RF | RF | Store Lost |  | 1 |  |  | 1
2 | 2021-10-09 13:47 | 2021-10-09 21:21 | 7.5667 | RF4 HVPS trip [RF] |  |  | 2021-10-09 21:21 | 2021-10-09 23:41 | 2.3333 | [9 empty] | 0
[7 empty] | 2021-10-09 21:21 | 2021-10-09 22:45 |  | 1.4 | RF | RF | RF | Store Lost |  | 1 |  |  | 1
[7 empty] | 2021-10-09 22:45 | 2021-10-09 23:41 |  | 0.93333 | MCR | MCR | MCR | Inhibits Beam To User |  |  |  | 1 | 1
4 | 2021-10-09 23:41 | 2021-10-11 08:00 | 32.3167 | Int Dump: End of Period |  |  |  |  | 0 | 0 |  |  |  | Scheduled |  |  | 1 |  | 1
|  |  | 164.55 | [5 empty] | 3.45 | 3.45 | [8 empty] | 0
5 | 2021-10-12 08:00 | 2021-10-13 02:14 | 18.2333 | S:BM Ground Fault [MOM] |  |  | 2021-10-13 02:14 | 2021-10-13 18:14 | 16 | 16 | MOM | MOM | MOM | Store Lost |  | 1 |  |  | 1
6 | 2021-10-13 18:14 | 2021-10-15 01:08 | 30.9 | RF-4 Anode OI [RF] |  |  | 2021-10-15 01:08 | 2021-10-15 02:19 | 1.1833 | 1.1833 | RF | RF | RF | Store Lost |  | 1 |  |  | 1
7 | 2021-10-15 02:19 | 2021-10-15 17:31 | 15.2 | RF-4 Anode OI [RF] |  |  | 2021-10-15 17:31 | 2021-10-15 18:26 | 0.91667 | 0.91667 | RF | RF | RF | Store Lost |  | 1 |  |  | 1
8 | 2021-10-15 18:26 | 2021-10-16 06:06 | 11.6667 | RF-4 Anode OI [RF] |  |  | 2021-10-16 06:06 | 2021-10-16 10:10 | 4.0667 | 4.0667 | RF | RF | RF | Store Lost |  | 1 |  |  | 1
11 | 2021-10-16 10:10 | 2021-10-18 08:00 | 45.8333 | Int Dump: End of Period |  |  |  |  | 0 | 0 |  |  |  | Scheduled |  |  | 1 |  | 1
|  |  | 121.8333 | [5 empty] | 22.1667 | 22.1667 | [8 empty] | 0
|  |  | 0 |  |  |  | 2021-10-19 08:00 | 2021-10-19 08:28 | 0.46667 | 0.46667 | AOP | AOP | AOP | Inhibits Beam to User | Orbit control issue |  |  | 1 | 1
12 | 2021-10-19 08:28 | 2021-10-21 16:59 | 56.5167 | RF-1 Kalmus trip [RF] |  |  | 2021-10-21 16:59 | 2021-10-21 18:05 | 1.1 | 1.1 | RF | RF | RF | Store Lost |  | 1 |  |  | 1
13 | 2021-10-21 18:05 | 2021-10-25 08:00 | 86.9167 | Int Dump: End of Period |  |  |  |  | 0 | 0 |  |  |  | Scheduled |  |  | 1 |  | 1
|  |  | 143.4333 | [5 empty] | 1.5667 | 1.5667 | [8 empty] | 0
14 | 2021-10-26 08:00 | 2021-11-01 08:00 | 144 | Int Dump: End of Period |  |  |  |  | 0 | 0 |  |  |  | Scheduled |  |  | 1 |  | 1
|  |  | 144 | [5 empty] | 0 | 0 | [8 empty] | 0
15 | 2021-11-02 08:00 | 2021-11-05 18:26 | 82.4333 | RF-4 Anode OI [RF] |  |  | 2021-11-05 18:26 | 2021-11-05 18:55 | 0.48333 | 0.48333 | RF | RF | RF | Store Lost |  | 1 |  |  | 1
16 | 2021-11-05 18:55 | 2021-11-08 08:00 | 61.0833 | Int Dump: End of Period |  |  |  |  | 0 | 0 |  |  |  | Scheduled |  |  | 1 |  | 1
|  |  | 143.5167 | [5 empty] | 0.48333 | 0.48333 | [8 empty] | 0
17 | 2021-11-09 08:00 | 2021-11-13 06:03 | 94.05 | RF airflow error [RF] |  |  | 2021-11-13 06:03 | 2021-11-13 06:58 | 0.91667 | 0.91667 | RF | RF | RF | Store Lost |  | 1 |  |  | 1
18 | 2021-11-13 06:58 | 2021-11-15 08:00 | 49.0333 | Int Dump: End of Period |  |  |  |  | 0 | 0 |  |  |  | Scheduled |  |  | 1 |  | 1
|  |  | 143.0833 | [5 empty] | 0.91667 | 0.91667 | [8 empty] | 0
19 | 2021-11-17 08:00 | 2021-11-20 20:47 | 84.7833 | S30B:H2 glitch [PS] |  |  | 2021-11-20 20:47 | 2021-11-20 21:59 | 1.2 | 1.2 | PS | PS | PS | Store Lost |  | 1 |  |  | 1
20 | 2021-11-20 21:59 | 2021-11-25 | 98.0167 | Int Dump: End of Period |  |  |  |  | 0 | 0 |  |  |  | Scheduled |  |  | 1 |  | 1
|  |  | 182.8 | [5 empty] | 1.2 | 1.2 | [8 empty] | 0
21 | 2021-11-26 08:00 | 2021-11-26 12:49 | 4.8167 | 26ID Orbit Error [AOP] |  |  | 2021-11-26 12:49 | 2021-11-26 13:47 | 0.96667 | 0.96667 | AOP | AOP | AOP | Store Lost |  | 1 |  |  | 1
22 | 2021-11-26 13:47 | 2021-12-01 14:45 | 120.9667 | S2A:H3 Glitch [PS] |  |  | 2021-12-01 14:45 | 2021-12-01 15:43 | 0.96667 | 0.96667 | PS | PS | PS | Store Lost |  | 1 |  |  | 1
23 | 2021-12-01 15:43 | 2021-12-05 02:55 | 83.2 | RF-4 Anode OI [RF] |  |  | 2021-12-05 02:55 | 2021-12-05 03:34 | 0.65 | 0.65 | RF | RF | RF | Store Lost |  | 1 |  |  | 1
24 | 2021-12-05 03:34 | 2021-12-06 08:00 | 28.4333 | Int Dump: End of Period |  |  |  |  | 0 | 0 |  |  |  | Scheduled |  |  | 1 |  | 1
|  |  | 237.4167 | [5 empty] | 2.5833 | 2.5833 | [8 empty] | 0
25 | 2021-12-08 08:00 | 2021-12-13 08:00 | 120 | Int Dump: End of Period |  |  |  |  | 0 | 0 |  |  |  | Scheduled |  |  | 1 |  | 1
|  |  | 120 | [5 empty] | 0 | 0 | [8 empty] | 0
26 | 2021-12-14 08:00 | 2021-12-21 08:00 | 168 | Int Dump: End of Period |  |  |  |  | 0 | 0 |  |  |  | Scheduled |  |  | 1 |  | 1
|  |  | 168 | [5 empty] | 0 | 0 | [8 empty] | 0
|  | Number of Lost Fills | 13 | [5 empty] | Downtime
|  | Number of Intentional Dumps | 8 | [5 empty] | User | System
|  | Number of Fills | 21 | [5 empty] | 32.3667 | 32.3667 | [5 empty] | 13 | 10 | 2 | 25
[16 empty] | SL | Scheduled | Inhibits
|  | Total User Beam | 1568.6333 | 65.3597 | User Beam days
|  | Total User Downtime | 32.3667 | <-- This downtime includes Gaps Open
|  | Total Schedule Run Length | 1601 | [12 empty] | #REF!
23
|  | Mean Time Between Faults | 120.6641
|  | Faults/Day of Delivered Beam | 0.1989 | [13 empty] | #N/A
|  | X-ray Availability | 97.98% | [13 empty] | #N/A
2

## Stats
Group
Data | PS | RF | AOP | MOM | MCR | Grand Total
Sum - Inhibits Beam | 0 | 0 | 1 | 0 | 1 | 2
Sum - Store Lost | 2 | 9 | 1 | 1 | 0 | 13
Sum of System Length | 2.1667 | 11.8333 | 1.4333 | 16 | 0.93333 | 32.3667
| RF | Diag | PS | Controls | Accelerator Intlks | Radiation Intlks | Water/ME | VAC | Operations | Physics | ID-FE | Electrical-APS | Electrical-ANL | Cooling-ANL | Other | Network | Unidentified | Grand Total | Total Hours
Run 2021-3 | 0.7391% |  | 0.1353% |  |  |  | 0.9994% |  | 0.0583% | #DIV/0! | [7 empty] | 2.022%
Budget | 0.54% | 0.12% | 0.54% | 0.3% | 0.28% | 0.28% | 0.36% | 0.36% | 0.12% | 0% | 0.06% | 0.06% | 0.06% | 0.06% | 0.18% | 0.12% | 0.06% | 3.5%
Hours for Run | 11.8333 |  | 2.1667 |  |  |  | 16 |  | 0.93333 | 1.4333 | [7 empty] | 32.3667
Faults | 9 |  | 2 |  |  |  | 1 |  | 0 | 1 | [7 empty] | 13
| RF | Diag | PS | Controls | Accelerator Intlks | Radiation Intlks | MOM | Operations | Physics | ID-FE | Electrical-APS | Electrical-ANL | Cooling-ANL | Other | Network | Unidentified
Run 2021-3 | 0.1377 | 0 | 0.0306 | 0 | 0 | 0 | 0.0153 | 0 | 0.0153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1989
Budget | 0.12 | 0.03 | 0.12 | 0.05 | 0.035 | 0.02 | 0.06 | 0.02 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.02 | 0.01 | 0.02 | 0.545
Total User Beam | 1568.6333
Total Schedule Run Length | 1601
Filter
Cause
Type | Data | PS | RF | MOM | AOP | MCR | Grand Total
Store Lost | Sum - Store Lost | 2 | 9 | 1 | 1 |  | 13
| Sum - Inhibits Beam | 0 | 0 | 0 | 0 |  | 0
Inhibits Beam To User | Sum - Store Lost |  |  |  | 0 | 0 | 0
| Sum - Inhibits Beam |  |  |  | 1 | 1 | 2
Total Sum - Store Lost |  | 2 | 9 | 1 | 1 | 0 | 13
Total Sum - Inhibits Beam |  | 0 | 0 | 0 | 1 | 1 | 2