Title
EPICS Database Principles
Andrew Johnson
APS Engineering Support Division

---
Outline
Outline
- Records
- Fields and field types
- Record Scanning
- Input and Output record types
- Links, link address types
- Connecting records together
- Protection mechanisms
- Alarms, dead-bands, simulation and security

---
Database = Records + Fields + Links
Database = Records + Fields + Links
- A control system using EPICS will contain one or more IOCs
- Each IOC loads one or more Databases telling it what to do
- A Database is a collection of Records of various types
- A Record is an object with:
  - A unique name
  - A behavior defined by its record type (class)
  - Controllable properties (fields)
  - Optional associated hardware I/O (device support)
  - Links to other records

---
Record Activity
Record Activity
- Records are active — they can do things:
  - Get data from other records or from hardware
  - Perform calculations
  - Check values are in range & raise alarms
  - Put data to other records or to hardware
  - Activate or disable other records
  - Wait for hardware signals (interrupts)
- What a record does depends upon its record type and the settings of its fields
- No action occurs unless a record is processed

---
How is a Record implemented?
How is a Record implemented?
- A ‘C’ structure with a data member for each record field
  - All records start with a standard set of fields (dbCommon) that the system needs, including pointers to record type information
- A record definition within a database provides
  - Record name
  - The record’s type
  - Values for each design field
- A record type provides
  - Definitions of all the fields
  - Code which implements the record’s behavior
- New record types can be added to an application as needed

---
A graphical view of a Record
A graphical view of a Record

---
Another graphical view of a Record
Another graphical view of a Record
The small CapFast symbol for an Analogue Output record

---
The IOC’s view
The IOC’s view
The full .db file entry for an Analogue Output Record
record(ao,"DemandTemp") {
  field(DESC,"Temperature")
  field(ASG,"")
  field(SCAN,"Passive")
  field(PINI,"NO")
  field(PHAS,"0")
  field(EVNT,"0")
  field(DTYP,"VMIC 4100")
  field(DISV,"1")
  field(SDIS,"")
  field(DISS,"NO_ALARM")
  field(PRIO,"LOW")
  field(FLNK,"")
  field(OUT,"#C0 S0")
  field(OROC,"0.0e+00")
  field(DOL,"")
  field(OMSL,"supervisory")
  field(HHSV,"NO_ALARM")
  field(LLSV,"NO_ALARM")
  field(HSV,"NO_ALARM")
  field(LSV,"NO_ALARM")
  field(HYST,"0.0e+00")
  field(ADEL,"0.0e+00")
  field(MDEL,"0.0e+00")
  field(SIOL,"")
  field(SIML,"")
  field(SIMS,"NO_ALARM")
  field(IVOA,"Continue normally")
  field(IVOV,"0.0e+00")
}
This slide only shows design fields; other fields exist which are only used at run-time
  field(OIF,"Full")
  field(PREC,"1")
  field(LINR,"NO CONVERSION")
  field(EGUF,"100")
  field(EGUL,"0")
  field(EGU,"Celcius")
  field(DRVH,"100")
  field(DRVL,"0")
  field(HOPR,"80")
  field(LOPR,"10")
  field(HIHI,"0.0e+00")
  field(LOLO,"0.0e+00")
  field(HIGH,"0.0e+00")
  field(LOW,"0.0e+00")

---
Fields are for...
Fields are for...
- Defining
  - What causes a record to process
  - Where to get/put data from/to
  - How to turn raw I/O data into a numeric engineering value
  - Limits indicating when to report an alarm
  - When to notify value changes to a client monitoring the record
  - A Processing algorithm
  - Anything else which needs to be set for each record of a given type
- Holding run-time data
  - Input or output values
  - Alarm status, severity and acknowledgments
  - Processing time-stamp
  - Other data for internal use

---
Field types
Field types — fields can contain:
- Integers
  - char, short or long
  - signed or unsigned
- Floating-point numbers
  - float or double
- Fixed length strings
  - maximum useful length is 40 characters
- Enumerated/menu choices
  - select one of up to 16 strings
  - stored as a short integer
- Arrays of any of the above types
- Links
  - to other records in this or other IOCs
  - to hardware signals (device support)
  - provide a means of getting or putting a value
- Other private data
  - not accessible remotely

---
All Records have these fields
All Records have these design fields
NAME	60 Character unique name (but using more than 28 can cause problems)
DESC	40 Character description
ASG	Access security group
SCAN	Scan mechanism
PHAS	Scan order (phase)
PINI	Process during IOC initialization?
PRIO	Scheduling priority
SDIS	Scan disable input link
DISV	Scan disable value
DISS	Disabled severity
FLNK	Forward link

---
All Records have Run-time fields
All Records have these Run-time fields
PROC	Force processing
PACT	Process active
STAT	Alarm status
SEVR	Alarm severity
TPRO	Trace processing
UDF	Non-zero if record value undefined
TIME	Time when record was last processed

---
Record Scanning
Record Scanning
- SCAN field is a menu choice from
  - Periodic — 0.1 seconds .. 10 seconds (extensible)
  - I/O Interrupt (if device supports this)
  - Soft event — EVNT field
  - Passive (default)
- The number in the PHAS field allows the relative order in which records are processed within a scan to be controlled
  - Records with PHAS=0 are processed first
  - Then those with PHAS=1 , PHAS=2 etc.
- The PINI field chooses if/when records get processed once at IOC startup or when paused
  - No, Yes, Run, Running, Pause, Paused
- PRIO field selects Low/Medium/High priority for Soft event and I/O Interrupts
- A record is also processed whenever any value is written to its PROC field

---
Input records often have these fields
Input records often have these fields
INP	Input link
DTYP	Device type
RVAL	Raw data value
VAL	Engineering value
LOPR	Low operator range
HOPR	High operator range

---
Analog I/O fields
Analogue I/O records have these fields:
EGU	Engineering unit string
LINR	Unit conversion control: No conversion, Linear, Slope,
        breakpoint table name
EGUL	Low engineering value
EGUF	High engineering value
ESLO	Unit conversion slope
EOFF	Unit conversion offset

---
Periodic Input
Periodically Scanned Analog Input
- Analogue Input “Temperature”
- Reads from the Xycom XY566 ADC Card 0 Signal 0
- Gets a new value every second
- Data is converted from ADC range to 0..120 Celsius

---
Interrupt Input
Interrupt Scanned Binary Input
- Binary Input “VentValve”
- Reads from Allen-Bradley TTL I/O Link 0, Adaptor 0, Card 3, Signal 5
- Processed whenever value changes
- 0 = “Closed”, 1 = “Open”
- Major alarm when valve open

---
Output records often have these fields
Most output records have these fields
OUT	Output link
DTYP	Device type
VAL	Engineering value
RVAL	Raw output value
DOL	Input link to fetch output value
OMSL	Output mode select:
Supervisory, Closed Loop
LOPR	Low operator range
HOPR	High operator range

---
Analog Output fields
Analogue outputs also have these fields:
OROC	Output rate of change
OIF	Incremental or Full output
OVAL	Output value
DRVH	Drive high limit
DRVL	Drive low limit
IVOA	Invalid output action
IVOV	Invalid output value
RBV	Read-back value

---
Passive Output
Passive Binary Output
- Binary Output “Solenoid”
- Controls Xycom XY220 Digital output Card 0 Signal 12
- Record is only processed by
  - Channel Access ‘put’ to a PP field (e.g. .VAL)
  - Another record writes to a PP field
  - Forward Link from another record
  - Another record reads this with PP

---
Break #1
Break time...
5 Minute break

---
Links
Links
A link is a type of field, and is one of
- Input link
  - Fetches data
- Output link
  - Writes data
- Forward link
  - Points to the record to be processed once this record finishes processing

---
Input and Output links may be...
Input and Output links may be...
Constant numeric value, e.g.:
0
3.1415926536
-1.6e-19
- Hardware link
  - A hardware I/O signal address (INP or OUT field only)
  - The address format depends on the device support layer
- Process Variable link — the name of a record, at run-time this becomes either
  - Database link
    - Target record must be present in this IOC
  - Channel Access link
    - Target record can be in a different IOC

---
Hardware links
Hardware links
VME_IO	#Cn Sn @parm
Card, Signal
INST_IO	@parm
CAMAC_IO	#Bn Cn Nn An Fn @parm
Branch, Crate, Node, Address, Function
AB_IO	#Ln An Cn Sn @parm
Link, Adapter, Card, Signal
GPIB_IO	#Ln An @parm
Link, Address
BITBUS_IO	#Ln Nn Pn Sn @parm
Link, Node, Port, Signal
BBGPIB_IO	#Ln Bn Gn @parm
Link, Bitbus Address, GPIB Address
VXI_IO	#Vn Cn Sn @parm
     or	#Vn Sn @parm
Frame, Slot, Signal

---
Database links
Database links
- These comprise:
  - The name of a record in this IOC
myDb:myRecord
  - An optional field name
    - .VAL	(default)
  - Process Passive flag
    - NPP	(default), or PP
  - Maximize Severity flag
    - NMS	No maximize severity (default)
    - MS	Maximize severity
    - MSS	Maximize Status and Severity (new in R3.14.11)
    - MSI	Maximize Severity when Invalid (new in R3.14.11)
- Example
  - M1:current.RBV NPP MS
- NB: Database links with the PP flag set never wait for asynchronous record processing to finish, so an input link that triggers a read from slow hardware will return the previous data in that record

---
Channel Access links
Channel Access links
- Similar to database links
- Name a record that can be located in a different IOC
- Use Channel Access to communicate with the target record
  - Just like any other CA client, even for local records
  - Input sets up a CA monitor on the channel
- May include a field name (default .VAL)
- PP Link flags are ignored
  - Input links are always NPP
  - Output links follow PP attribute of destination field
  - These are how all CA clients behave
- MS Link flags apply to Input links
  - Input links honor NMS (default)/MS/MSS/MSI
  - Output links are always NMS
- Additional flags for CA links
  - CA	Forces a “local” link to use CA
  - CP	On input link, process this record on CA monitor event
  - CPP	Like CP but only process me if SCAN is Passive

---
Link flag summary
Chapter 5 of the IOC Application Developer’s Guide covers
record links and scanning in detail, and is worth reading.

---
Device Support
Device Support
- Records do not access hardware directly
- The Device Support layer performs I/O operations on request
  - Each device support performs I/O for one record type
- A record’s DTYP field determines which device support it uses
  - Most record types default to Soft Channel support if you don’t set DTYP
- The device support selected determines the format of the link (INP or OUT field) containing the device address
- Adding new device support does not require any changes or recompilation of the record type code
- Device support often calls other software to do work for it (Driver Support or other libraries)

---
Synchronous vs Asynchronous I/O
Synchronous vs Asynchronous I/O
- IOC rules do not allow device support to busy-wait (i.e. delay record processing while waiting for the results of a slow I/O operation)
  - Fast I/O can be handled synchronously
  - Slow operations must operate asynchronously
- Register-based VME/PCI cards usually give a fast response (<10µs), so should be synchronous
  - When called, a synchronous read or write call to device support completes all I/O operations needed before returning
- Serial, network or field-bus I/O usually takes some time (>10ms) to return data, so should be asynchronous
  - Asynchronous device support starts an I/O operation when the record calls it, flagging it as incomplete by setting PACT to true before returning
  - When the results are available (discovered by a CPU interrupt or polling background thread), the device support must call the record’s process() routine to finish the record processing operations

---
Soft Device Support
Soft Device Support
- “Hard” input and output records do hardware I/O via device support
- “Soft” records access data from other records via DB or CA links
- 2 or 3 kinds of support are provided in recent R3.14 releases:
  - Soft Channel
    - Get/Put VAL through link, no units conversion performed
  - Async Soft Channel (currently output records only)
    - Put VAL through CA link, no conversions, wait for completion
  - Raw Soft Channel
    - Inputs
      - Get RVAL via input link
      - Convert RVAL to VAL (record-type specific)
    - Outputs
      - Convert VAL to RVAL (record-type specific)
      - Put RVAL to output link

---
Forward links
Forward links
- Usually a Database link, referring to a record in same IOC
- No flags (PP, MS etc.), although VDCT includes them erroneously
- Destination record is only processed if its SCAN field is Passive
- Does not pass a value, just causes subsequent processing
- Forward linking to another IOC via Channel Access is possible, but the link must explicitly name the PROC field of the remote record
  - In this case only, the remote record does not need to have SCAN set to Passive

---
Processing chains
Processing chains

---
Which record is never processed?
Which record is never processed?

---
How often is Input_1 processed?
How often is Input_1 processed?

---
The PACT field
The PACT field
- All records have a boolean run-time field PACT (Process Active)
- PACT breaks loops of linked records
- It is set to true early in the act of processing the record (but it's not the first thing that the process routine does)
  - PACT must be true whenever a link from that record is used
- PACT gets reset to false after all record I/O and forward link processing have finished
- A PP link can never process a record that has PACT true
  - Input links take the current value from the target field
  - Output links put their value to the target field
    - In some cases they ask the target record to reprocess itself again later
  - Forward links do nothing

---
What happens here?
What happens here?

---
Preventing records from processing
Preventing records from processing
- It is useful to be able to stop an individual record from processing on some condition
- Before record-specific processing is called, a value is read through the SDIS input link into DISA (0 if the link is not set)
- If DISA=DISV, the record will not be processed
- The default value of the DISV field is 1
- A disabled record may be put into an alarm state by giving the desired severity in the DISS field
- The FLNK of a disabled record is never triggered

---
Break #2
Break time...
5 Minute break

---
Order of Operations (Sync) #1
Order of Operations (Synchronous I/O)
Every 0.1 seconds, iocCore will attempt to process the Output_1 record
The Output_1.PACT field is currently False, so the record is quiescent and can be processed
1. If set, the Output_1.SDIS link would be read into Output_1.DISA
2. Since DISA≠DISV, the ao record type's process() routine is called

---
Order of Operations (Sync) #2
Order of Operations (Synchronous I/O)
1. The ao's process() routine checks the Output_1.OMSL field; it is closed_loop, so
2. It sets Output_1.PACT to True, then
3. Reads a value through the Output_1.DOL link
4. The Output_1.DOL link contains Calculation_1.VAL PP so this first attempts to process the Calculation_1 record

---
Order of Operations (Sync) #3
Order of Operations (Synchronous I/O)
1. The Calculation_1.SCAN field is Passive and Calculation_1.PACT is False, so processing is possible
2. If set, the Calculation_1.SDIS link would be read into DISA
3. Since DISA≠DISV, the calc record type's process() routine is called

---
Order of Operations (Sync) #4
Order of Operations (Synchronous I/O)
1. The calc's process() routine sets Calculation_1.PACT to True, then
2. Starts a loop to read values from the links INPA through INPL
3. The Calculation_1.INPA link is set to Input_1.VAL PP so this first attempts to process the Input_1 record

---
Order of Operations (Sync) #5
Order of Operations (Synchronous I/O)
1. The Input_1.SCAN field is Passive and Input_1.PACT is False, so processing is possible
2. If set, the Input_1.SDIS link is read into the Input_1.DISA field
3. Since DISA≠DISV, the ai record type's process() routine is called
4. The ai process() calls the associated device support to read a value from the hardware it's attached to

---
Order of Operations (Sync) #6
Order of Operations (Synchronous I/O)
1. The device support is synchronous, so it puts the hardware input value into the Input_1.RVAL field and returns to the ai record's process() code
2. The Input_1.PACT field is set to True
3. The record's timestamp field Input_1.TIME is set to the current time
4. The raw value in Input_1.RVAL is converted to engineering units, smoothed, and the result put into the Input_1.VAL field

---
Order of Operations (Sync) #7
Order of Operations (Synchronous I/O)
1. The Input_1.VAL is checked against alarm limits and monitor dead-bands, and appropriate actions is taken if these are exceeded
2. If the Forward Link field Input_1.FLNK is set, an attempt is made to process the record it points to
3. The Input_1.PACT field is set to False, and the process() routine returns control to the Calculation_1 record

---
Order of Operations (Sync) #8
Order of Operations (Synchronous I/O)
1. The value read through the Calculation_1.INPA link is copied into the Calculation_1.A field
2. The Calculation record type's process() routine continues to loop, reading its input links
3. In this example only the INPA link is set, so the routine finishes the loop and evaluates the Calculation_1.CALC expression (not shown)
4. The result of the expression is put in the Calculation_1.VAL field

---
Order of Operations (Sync) #9
Order of Operations (Synchronous I/O)
1. The record's timestamp field Calculation_1.TIME is set to the current time
2. Calculation_1.VAL is checked against alarm limits and monitor dead-bands, and appropriate action is taken if these are exceeded
3. If the Forward Link field Calculation_1.FLNK is set, an attempt is made to process the record it points to
4. The Calculation_1.PACT field is set to False, and the process() routine returns control to the Output_1 record

---
Order of Operations (Sync) #10
Order of Operations (Synchronous I/O)
1. The value read through the Output_1.DOL link would now be forced into the range DRVL..DRVH if those fields were set, but they aren't so it's copied to the Output_1.VAL field unchanged
2. The Output_1.VAL value is converted from engineering to raw units and placed in Output_1.RVAL
3. Output_1.VAL is checked against alarm limits and monitor dead-bands, and appropriate action is taken if these are exceeded
4. The associated device support is called to write the value to the hardware

---
Order of Operations (Sync) #11
Order of Operations (Synchronous I/O)
1. The device support is synchronous, so it outputs the value to the attached hardware and returns
2. The record's timestamp field Output_1.TIME is set to the current time
3. If the Forward Link field Output_1.FLNK is set, an attempt is made to process the record it points to
4. The Output_1.PACT field is set to False, and the process() routine returns

---
How are records given CPU time?
How are records given CPU time?
Many different IOC threads are used to process records:
- scanperiod — Periodic scans
  - Each scan rate gets its own thread
  - Faster scans at higher thread priority (if supported by the Operating System)
- cbLow, cbMedium, dbHigh — Callback facility
  - One thread for each scheduling priority (PRIO field)
  - Used by device support, I/O Interrupts etc.
- scanOnce
  - IOC internal use for record reprocessing
- CAS-client — CA client-initiated processing
  - One thread for each CA client connected to the server
- Channel Access threads use lower priority than record processing
  - If a CPU spends all its time doing I/O and record processing, you may be unable to control or monitor the IOC via the network

---
What could go wrong here?
What could go wrong here?

---
Lock-sets
Lock-sets
- Prevent records from being processed simultaneously by two different scan tasks
  - PACT can’t do that, it isn’t set early enough and is not a Mutex
- A lock-set is a group of records interconnected by database links
- Lock-sets are determined automatically by the IOC at start-up, or whenever a database link is added, deleted or modified
- You can split two linked records into different lock sets by making the link(s) joining them into Channel Access ones, using the CA flag
  - Remember that CA links behave slightly differently than DB links, make sure your design still works!

---
Alarms
Alarms
- Every record has the fields
  - SEVR	Alarm Severity
    - NONE, MINOR, MAJOR, INVALID
  - STAT	Alarm Status (reason)
    - READ, WRITE, UDF, HIGH, LOW, STATE, COS, CALC, DISABLE, etc.
- Most numeric records compare VAL against the HIHI, HIGH, LOW and LOLO fields after its value has been determined
- The HYST field sets a hysteresis to prevent alarm chattering
- A separate alarm severity can be set for each numeric limit exceeded
  - Fields HHSV, HSV, LSV, and LLSV
- Discrete (binary) records can raise alarms on entering a particular state, or on a change of state (COS)

---
Change Notification: Monitor Deadbands
Change Notification: Monitor Dead-bands
- Channel Access notifies clients that are monitoring a numeric record when
  - VAL changes by more than the value in field:
MDEL	Value monitors
ADEL	Archive monitors
  - Record’s Alarm Status changes
HYST	Alarm hysteresis
The Analogue Input record has a smoothing filter to reduce noise on the input signal (SMOO)

---
Breakpoint Tables
Breakpoint Tables
Type J Thermocouple
Raw Input, ADC Units
Engineering Value, Celcius
- Analogue Input and Output records can do non-linear conversions from/to the raw hardware value
- Breakpoint tables interpolate values from a given table
- To use, set the record’s LINR field to the name of the breakpoint table you want to use
- Example breakpoint table (in some loaded .dbd file)
breaktable(typeKdegC) {
       0.000000 0.000000
     299.268700 74.000000
     660.752744 163.000000
    1104.793671 274.000000
    1702.338802 418.000000
    2902.787322 703.000000
    3427.599045 831.000000
    ...
}

---
Simulation
Simulation
Input and output record types often allow simulation of hardware interfaces
SIML	Simulation mode link
SIMM	Simulation mode value
SIOL	Simulation input link
SVAL	Simulated value
SIMS	Simulation alarm severity
- Before calling device support, records read SIMM through the SIML link
- If SIMM=YES (1) or SIMM=RAW (2) the device support is not used; record I/O is done through the SIOL link and SVAL field instead
- An alarm severity can be set whenever simulating, given by SIMS field

---
Access Security
Access Security
- A networked control system must have the ability to enforce security rules
  - Who can do what from where, and when?
- In EPICS, security is enforced by the CA server (the IOC or gateway)
- A record is placed in the Access Security Group named in its ASG field
  - DEFAULT is used if no group name is given
- Rules are specified for each group to determine whether a CA client can read or write to records in that group, based on
  - Client user ID
  - Client host-name or IP address
  - Access Security Level of the field addressed
  - Values read from the database

---
Access Security Configuration File
Access Security Configuration File
Security rules are loaded from an Access Security Configuration File, for example:
UAG(users) {anj, mrk, jba, nda}
HAG(hosts) {tux.aps.anl.gov, earth, venus, gaia}
ASG(DEFAULT) {
    RULE(1, READ)
    RULE(1, WRITE) {
        UAG(users)
        HAG(hosts)
    }
}
- If no security file is loaded, Security will be turned off and nothing refused
- For more details and the rule syntax, see Chapter 8 of the IOC Application Developers Guide