Title
State Notation Language and the Sequencer
Andrew Johnson
APS Engineering Support Division

---
Outline
Outline
- What is State Notation Language (SNL)
- Where it fits in the EPICS toolkit
- Components of a state notation program
- Some notes on the Sequencer runtime
- Building, running and debugging a state notation program
- Additional features
- When to use it
- This talk does not cover all the features of the sequencer
- Consult the reference manual for more information
  - http://www-csr.bessy.de/control/SoftDist/sequencer/

---
SNL and the Sequencer
SNL and the Sequencer
- The sequencer runs programs written in State Notation Language (SNL)
- SNL is a ‘C’ like language to facilitate programming of sequential operations
- Fast execution using compiled code
- Programming interface to extend EPICS in the real-time environment
- Common uses
  - Automated start-up and sequencing for subsystems like vacuum or RF where coordination of multiple components needed
  - Provide fault recovery or transition to a safe state
  - Provide automatic calibration of equipment

---
Where’s the Sequencer?
Where is the Sequencer?
LAN
Channel Access
IOC
Sequencer
Database
Device Support
I/O Hardware

---
Where’s the Sequencer Now?
Where is the Sequencer?
Tools
MEDM
Client
Client
Client
MEDM
Sequencer
LAN
Server
IOC
IOC
IOC
Meter
Power Supply
Camera

---
The Best Place for the Sequencer
The Best Place for the Sequencer
- Traditionally sequencers run in the IOC
- Recent versions can be run either within an IOC or as a standalone program on a workstation
- Locating them within the IOC they control makes them easier to manage and independent of network issues
- Running them on a workstation can make testing and debugging easier
- On a workstation, SNL provides an easy way to write simple CA client programs

---
Some Definitions
Some Definitions
- SNL: State Notation Language
- SNC: State Notation Compiler
- Sequencer: The tool that executes the compiled SNL code
- Program: A complete SNL application, consisting of declarations and one or more state sets
- State Set: A set of states that make a complete finite state machine
- State: A particular mode of the state set in which it remains until one of its transition conditions evaluates to TRUE

---
SNL implements State Transition Diagrams
SNL implements State Transition Diagrams
State A
Event
Transition
A to B
Action
State B

---
STD Example
Example State Transition Diagram
Start
Low vacuum
pressure < 4.9 µTorr
open valve, turn on cryo pump
High vacuum
pressure > 5.1 µTorr
close valve, turn off cryo pump

---
SNL: General Structure and Syntax
SNL: General Structure and Syntax
program program_name
declarations
ss state_set_name {
    state state_name {
entry {
    entry action statements
}
when (event) {
    action statements
} state next_state_name
when (event) {
   ...
   } state next_state_name
exit{
    exit action statements
}
}
state state_name {
...
}
}

---
SNL: General Structure and Syntax
program name	A program may contain multiple state sets. The program name is used as a handle to the sequencer manager for state programs.
ss name {	Each state set becomes a separate task or thread.
state name {	A state is somewhere the task waits for events. When an event occurs it checks to see which action it should execute. The first state defined in a state set is the initial state.
option flag;	A state-specific option.
when (event) {	Define events for which this state waits.
} state next	Specifies the state to go to when these actions are complete.
entry {actions}	Actions to do on entering this state. With option -e; it will do these actions even if it enters from the same state.
exit {actions}	Actions to do on exiting this state. With option -x; it will do these actions even if it exits to the same state.

---
Declarations
Declarations – Variables
- Appear before a state set and have a scope of the entire program.
- Scalar variables
int	var_name;
short	var_name;
long	var_name;
char	var_name;
float	var_name;
double	var_name;
string	var_name; /* 40 characters */
Array variables: 1 or 2 dimensions, no strings
int	var_name[num_elements];
short	var_name[num_elements];
long	var_name[num_elements];
char	var_name[num_elements];
float	var_name[num_elements];
double	var_name[num_elements];

---
Declarations - Assignments
Declarations – Assignments
Assignment connects a variable to a channel access PV name
float pressure;
assign pressure to "CouplerPressureRB1";
double pressures[3];
assign pressures to {"CouplerPressureRB1", "CouplerPressureRB2", " CouplerPressureRB3"};
To use these channels in when clauses, they must be monitored
monitor pressure;
monitor pressures;
Use preprocessor macros to aid readability:
#define varMon(t,n,c) t n; assign n to c; monitor n;
varMon(float, pressure, "PressureRB1")

---
Declarations – Event Flags
Declarations – Event Flags
- Event flags are used to communicate events between state sets, or to receive explicit event notifications from Channel Access
- Declare them like this:
evflag	event_flag_name;
An event flag can be synchronized with a monitored variable
sync	var_name event_flag_name;
The flag will then be set when a monitor notification arrives, e.g.
evflag	pressure_event;
sync	pressure pressure_event;

---
Events
Events
Event: A specific condition on which associated actions are run and a state transition is made.
Possible events:
Change in value of a variable that is being monitored:
when (achan < 10.0)
A timer event (this is not a task delay!):
when (delay(1.5))
  - The delay time is in seconds and is a double; literal constant arguments to the delay function must contain a decimal point.
  - The timer starts when the state containing it was entered.
  - Use the state specific option -t; to stop it from being reset when transitioning to the same state.

---
Events (continued)
Events (continued)
The state of an event flag:
when (efTestAndClear(myflag))
when (efTest(myflag))
  - efTest() does not clear the flag. efClear() must be called sometime later to avoid an infinite loop.
  - If the flag is synced to a monitored variable, it will be set when the channel sends a value update
  - The event flag can also be set by any state set in the program using efSet(event_flag_name)
- Any change in the channel access connection status:
when (pvConnectCount() < pvChannelCount())
when (pvConnected(mychan))
Any combination of the above event types

---
Actions
Action Statements
- Built-in action function, e.g. :
  - pvPut(var_name);
  - pvGet(var_name);
  - efSet(event_flag_name);
  - efClear(event_flag_name);
- Almost any valid C statement
  - switch() is not implemented and code using it must be escaped.
%% escapes one line of C code
%{
escape any number of lines of C code
}%

---
Example - State Definitions and Transitions
Example – State Definitions and Transitions
Initial State
pressure > .0000051
      RoughPump on
      CryoPump off
      Valve closed
pressure <= .0000049
      RoughPump off
      CryoPump on
      Valve open
pressure <= .0000049
      RoughPump off
      CryoPump on
      Valve open
Low Vacuum
High Vacuum
pressure > .0000051
      RoughPump on
      CryoPump off
      Valve closed
10 minutes
      RoughPump off
      CryoPump off
      Valve closed
Fault

---
Example - Declarations
Example – Declarations
double pressure;
assign pressure to "Tank1Coupler1PressureRB";
monitor pressure;
short	RoughPump;
assign RoughPump to "Tank1Coupler1RoughPump";
short	CryoPump;
assign CryoPump to "Tank1Coupler1CryoPump";
short	Valve;
assign Valve to "Tank1Coupler1IsolationValve";
string CurrentState;
assign CurrentState to "Tank1Coupler1VacuumState";

---
Example – State Transitions
Example – State Transitions, Actions Omitted
program vacuum_control
ss coupler_control
{
state init{
when (pressure > .0000049){
} state low_vacuum
when (pressure <= .0000049){
} state high_vacuum
}
state high_vacuum{
when (pressure > .0000051){
} state low_vacuum
}
state low_vacuum{
when (pressure <= .0000049){
} state high_vacuum
when (delay(600.0)){
} state fault
}
state fault {
}
}

---
Example – Init State
Example – Initial State
state init {
entry {
strcpy(CurrentState,"Init");
pvPut(CurrentState);
}
when (pressure > .0000049){
RoughPump = 1;
pvPut(RoughPump);
CryoPump = 0;
pvPut(CryoPump);
Valve = 0;
pvPut(Valve);
} state low_vacuum
when (pressure <= .0000049){
RoughPump = 0;
pvPut(RoughPump);
CryoPump = 1;
pvPut(CryoPump);
Valve = 1;
pvPut(Valve);
} state high_vacuum
}

---
Example – State low_vacuum
Example – State low_vacuum
state low_vacuum{
entry {
strcpy(CurrentState,"Low Vacuum");
pvPut(CurrentState);
}
when (pressure <= .0000049){
RoughPump = 0;
pvPut(RoughPump);
CryoPump = 1;
pvPut(CryoPump);
Valve = 1;
pvPut(Valve);
} state high_vacuum
when (delay(600.0)){
} state fault
}

---
Example – State high_vacuum
Example – State high_vacuum
state high_vacuum{
entry {
strcpy(CurrentState,"High Vacuum");
pvPut(CurrentState);
}
when (pressure > .0000051){
RoughPump = 1;
pvPut(RoughPump);
CryoPump = 0;
pvPut(CryoPump);
Valve = 0;
pvPut(Valve);
} state low_vacuum
}

---
Example – State fault
Example – State fault
state fault{
entry{
strcpy(CurrentState,"Vacuum Fault");
pvPut(CurrentState);
}
}

---
Building an SNL program
Building an SNL program
- Use editor to build the source file. File name must end with
  “.st” or “.stt”, e.g. “example.st”
- “make” automates these steps:
  - Runs the C preprocessor on “.st” files, but not on “.stt” files.
  - Compiles the state program with SNC to produce C code:
    - snc example.st -> example.c
  - Compiles the resulting C code with the C compiler:
    - cc example.c -> example.o
  - The object file example.o becomes part of the application library, ready to be linked into an IOC binary.
  - The executable file “example” can be created instead.

---
Run Time Sequencer
Run Time Sequencer
- The sequencer executes the state program
- It is implemented as an event-driven application; no polling is needed
- Each state set becomes an operating system thread
- The sequencer manages connections to database channels through Channel Access
- It provides support for channel access get, put, and monitor operations
- It supports asynchronous execution of delays, event flag, pv put and pv get functions
- Only one copy of the sequencer code is required to run multiple programs
- Commands are provided to display information about the state programs currently executing

---
Executing a State Program – IOC
Executing a State Program
From an IOC console
On vxWorks:
seq &vacuum_control
On other operating systems:
seq vacuum_control
- To stop the program
  - seqStop "vacuum_control"

---
Debugging
Debugging
Use the sequencer's query commands:
seqShow
displays information on all running state programs
seqShow vacuum_control
displays detailed information on program
seqChanShow vacuum_control
displays information on all channels
seqChanShow vacuum_control,"-"
displays information on all disconnected channels
seqcar
displays information on all channel access channels

---
Debugging (continued)
Debugging (continued)
Use printf functions to print to the console
printf("Here I am in state xyz \n");
Put strings to pvs
sprintf(seqMsg1, "Here I am in state xyz");
pvPut(seqMsg1);
On vxWorks you can reload and restart
seqStop vacuum_control
... edit, recompile ...
ld < example.o
seq &vacuum_control

---
Additional Features
Additional Features
Connection management:
when (pvConnectCount() != pvChannelCount())
when (pvConnected(Vin))
Macros:
assign Vout to "{unit}:OutputV";
  - must use the +r compiler options for this if more than one copy of the sequence is running on the same ioc
seq &example, "unit=HV01"
- Some common SNC program options:
  - +r make program reentrant (default is -r)
  - -c don't wait for all channel connections (default is +c)
  - +a asynchronous pvGet() (default is -a)
  - -w don't print compiler warnings (default is +w)

---
Additional Features (continued)
Additional Features (continued)
Access to channel alarm status and severity:
pvStatus(var_name)
pvSeverity(var_name)
Queued monitors save CA monitor events in a queue in the order they come in, rather than discarding older values when the program is busy
syncQ var_name to event_flag_name [queue_length]
pvGetQ(var_name)
    - removes oldest value from variable's monitor queue. Remains true until queue is empty.
pvFreeQ(var_name)

---
Advantages
Advantages of SNL
- Can implement complicated algorithms
- Can stop, reload, restart a sequence program without rebooting
- Interact with the operator through string records and mbbo records
- C code can be embedded as part of the sequence
- All Channel Access details are taken care of for you
- File access can be implemented as part of the sequence

---
When to use the sequencer
When to use the sequencer
- For sequencing complex events
- E.g. parking and unparking a telescope mirror
Photograph courtesy of the Gemini Telescopes project

---
Should I Use the Sequencer?
Should I Use the Sequencer?
START
CAN I DO THIS IN A DB?
Y
N
CAN I DO THIS IN A DB?
Y
N
USE THE SEQUENCER
USE A DATABASE
END

---
Acknowledgements
Acknowledgments
- Slides for this presentation have been taken from talks prepared by the following people
  - Bob Dalesio (LANL/SNS/LCLS)
  - Deb Kerstiens (LANL)
  - Rozelle Wright (LANL)
  - Ned Arnold (Argonne)
  - John Maclean (Argonne)