Channel Access & Client Tools
Channel Access and Client Tools
Author:	Kenneth Evans, Jr., August 2004
Modified:	Kay Kasemir, October 2006
Andrew Johnson, January 2007

---
EPICS Overview
EPICS Overview
EDM
MEDM
Client
Client
Probe
ALH
Channel Access
Server
IOC
IOC
IOC
Meter
Power Supply
Camera
Client Tools

---
Channel Access
Channel Access
The EPICS “software bus”
Used to read and write values to/from Process Variables
To many people, Channel Access is EPICS
  - Especially those that have no IOC experience
  - “Integrate X into EPICS” often means “Be able to control X via CA”
CA is not defined by a protocol specification
  - Jeff Hill (LANL) maintains the CA client and server libraries
  - A single expert maintainer for both ensures very robust control systems

---
What is a Process Variable (PV)
“A named item of data, with associated optional attributes”
  - Data is an Integer, Floating point number, enumeration value or string, or an array of any of those types
  - Attributes include timestamp, alarm status/severity, precision, engineering units string, list of enumeration strings, operator/control/ alarm limits

---
Channel Access in One Slide
“connection request” or “search request”
“connection request” or “search request”
“get” or
“caGet”
“get” or
“caGet”
“put” or
“caPut”
“put” or
“caPut”
“set a monitor”
“set a monitor”
Who has a PV named “S1A:H1:CurrentAO”?
Who has a PV named “S1A:H1:CurrentAO”?
Change its value to 30.5
Change its value to 30.5
Notify me when the value changes
Notify me when the value changes
What is its value?
What is its value?
Channel Access Client
Channel Access Client
CA Client
CA Client
CA Server
CA Server
Channel Access Server
Channel Access Server
I do.
I do.
25.5 AMPS
25.5 AMPS
OK, it is now 30.5
OK, it is now 30.5
It is now 20.5 AMPS
It is now 20.5 AMPS
It is now 10.5 AMPS
It is now 10.5 AMPS
It is now -0.0023 AMPS
It is now -0.0023 AMPS
Process Variables:
Process Variables:
“put complete”
“put complete”
“post an event”
or
“post a monitor”
“post an event”
or
“post a monitor”
S1A:H1:CurrentAO
S1:P1:x
S1:P1:y
S1:G1:vacuum
S1A:H1:CurrentAO
S1:P1:x
S1:P1:y
S1:G1:vacuum
30.5 is too high. It is now set to the maximum value of 27.5.
30.5 is too high. It is now set to the maximum value of 27.5.
or
or
You are not authorized to change this value
You are not authorized to change this value
or
or

---
Tools Covered in This Presentation
Tools Covered in This Presentation
Command-Line Tools
  - caget, caput, camonitor, cainfo
Probe
StripTool
MEDM
ALH

---
More Information
More Information
There is a wealth of information in the EPICS web pages
  - http://www.aps.anl.gov/epics/index.php
Each of the Extensions covered here has its own page with much additional information
  - Including tar files of the latest releases
The are many other tools described there as well
The Extensions executables are typically located at
  - …epics/extensions/bin/<platform>/<executable>
  - e.g. /opt/epics/extensions/bin/solaris-sparc/edm
  - Platforms are solaris-sparc, linux-x86, win32-x86, etc.
The Base command line tools are typically at
  - …epics/base/bin/<platform>/<executable>

---
EPICS Extensions Web Page
EPICS Extensions Web Page

---
Command-Line Tools
Command-Line Tools
There used to be several versions of these tools
We will discuss the ones that now come with EPICS Base
The tools we will cover are:
  - caget
    - Gets the value of one or more process variables
  - caput
    - Sets the value of one process variable
  - camonitor
    - Monitors the value changes of one or more process variables
  - cainfo
    - Gets information about one or more process variables
All accept –h to display usage and options

---
Caget Example
Caget Example
Get the values of two process variables
  - caget S35DCCT:currentCC S:SRlifeTimeHrsCC
Returns
  - S35DCCT:currentCC 102.037
  - S:SRlifeTimeHrsCC 7.46514

---
Caput Example
Caput Example
Set the value of a process variable
  - caput Xorbit:S1A:H1:CurrentAO 1.2
Returns
  - Old : Xorbit:S1A:H1:CurrentAO 0
  - New : Xorbit:S1A:H1:CurrentAO 1.2

---
Camonitor Example
Camonitor Example
Monitor two process variables
  - camonitor evans:calc evans:bo01
Returns
  - evans:calc 2004-08-05 17:23:04.623245 1
  - evans:bo01 2004-08-05 17:23:04.623245 On
  - evans:calc 2004-08-05 17:23:05.123245 2
  - evans:bo01 2004-08-05 17:23:05.123245 Off
  - evans:calc 2004-08-05 17:23:05.623245 3
  - evans:calc 2004-08-05 17:23:06.123245 4
  - evans:calc 2004-08-05 17:23:06.623233 5
  - evans:calc 2004-08-05 17:23:07.123183 6
Use Ctrl-C to stop monitoring

---
Cainfo Example
Cainfo Example
Get information about a process variable
  - cainfo S35DCCT:currentCC
Returns
  - State: connected
  - Host: ctlapps4l188:5064
  - Access: read, no write
  - Data type: DBR_DOUBLE (native: DBF_DOUBLE)
  - Element count: 1
Some additional information can be found using Probe

---
Probe
Probe
Simple way to get information about a single process variable
Combines the features of caget, caput, camonitor, and cainfo in a graphical interface
Very useful in diagnosing problems

---
Probe Demo
Probe Demo
Macromedia Flash Demonstration of Probe

---
StripTool
Plots process variables in real time on a strip chart
Widely used

---
StripTool Demo
Macromedia Flash Demonstration of StripTool

---
MEDM
MEDM
Stands for Motif Editor and Display Manager
The principal human interface to the APS control system
Used worldwide at many facilities
Creates and runs control screens
[Speaker Notes: 01/11/07]

---
MEDM Screens
MEDM Screens
And thousands of others

---
MEDM
MEDM is very reliable at both design and run-time
However it is very hard to extend
  - Not written in Object-Oriented style
  - Maintainer has recently moved to other responsibilities
APS will only fix major bugs found in MEDM now
Not a good choice for a new control system
  - Use EDM instead (upcoming lecture)

---
ALH
ALH
Stands for Alarm Handler
Important GUI application in the APS Control Room
Brings alarms to the operators’ attention
  - It dings and flashes
Can be configured to require the operator to acknowledge alarms
Provides a hierarchical display
  - Allows managing alarms in overview or in detail
Provides guidance for handling specific alarms
Logs alarms and displays alarm history

---
ALH
ALH will be covered more fully in another lecture