ASYN Device Support Framework
ASYN/StreamDevice Support Frameworks
Eric Norum

---
ASYN
ASYN
- What is it?
- What does it do?
- How does it do it?
- How do I use it?

---
What is it?
What is it?
Asynchronous Driver Support is a general purpose facility for interfacing device specific code to low level communication drivers

---
asyn Architecture
asyn Architecture
Device support (or SNL code, another driver, or non-EPICS software)
Interfaces (named; pure virtual functions)
asynCommon (connect, report, …)
asynOctet (write, read, setInputEos,…)
Port (named object)
Port driver
addr=1
addr=0
device
device

---
Control flow – asynchronous driver
Control flow – asynchronous driver

---
Control flow – synchronous driver
Control flow – synchronous driver

---
ASYN Components – asynManager
ASYN Components – asynManager
Provides thread for each communication interface
  - All driver code executes in the context of this thread
Provides connection management
  - Driver code reports connect/disconnect events
Queues requests for work
  - Nonblocking – can be called by scan tasks
  - User-supplied callback code run in worker-thread context makes calls to driver
  - Driver code executes in a single-threaded synchronous environment
Handles registration
  - Low level drivers register themselves
  - Can ‘interpose’ processing layers

---
ASYN Components – asynCommon
ASYN Components – asynCommon
A group of methods provided by all drivers:
  - Report
  - Connect
  - Disconnect
  - Set option
  - Get option
    - Options are defined by low-level drivers
    - e.g., serial port rate, parity, stop bits, handshaking

---
ASYN Components – asynOctet
ASYN Components – asynOctet
- Driver or interposed processing layer
- Methods provided in addition to those of asynCommon:
  - Read
  - Write
  - Set end-of-string character(s)
  - Get end-of-string character(s)
- All that’s needed for serial ports, ‘telnet-style’ TCP/IP devices, USB-TMC.
- The single-threaded synchronous environment makes driver development much easier
  - No fussing with mutexes
  - No need to set up I/O worker threads

---
ASYN Components – asynGpib
ASYN Components – asynGpib
Methods provided in addition to those of asynOctet:
  - Send addressed command string to device
  - Send universal command string
  - Pulse IFC line
  - Set state of REN line
  - Report state of SRQ line
  - Begin/end serial poll operation
Interface includes asynCommon and asynOctet methods
  - Device support that uses read/write requests can use asynOctet drivers. Single device support source works with serial or GPIB.

---
ASYN Components – asynRecord
ASYN Components – asynRecord
Diagnostics
  - Set device support and driver diagnostic message masks
  - No more ad-hoc ‘debug’ variables!
General-purpose I/O
  - Replaces synApps serial record and GPIB record
Provides much of the old ‘GI’ functionality
  - Type in command, view reply
  - Works with all asyn drivers
A single record instance provides access to all devices in IOC

---
asynRecord
asynRecord
- EPICS record that provides access to most features of asyn, including standard I/O interfaces
- Applications:
  - Control tracing (debugging)
  - Connection management
  - Perform interactive I/O
- Very useful for testing, debugging, and actual I/O in many cases
- If your IOC uses ASYN it should provide at least one asynRecord to give clients control of diagnostic messages!

---
asynRecord – asynOctet devices
asynRecord – asynOctet devices
Configure serial port parameters
Interactive I/O to serial device
Perform GPIB-specific operations

---
asynRecord – register devices
asynRecord – register devices
Same asynRecord, change to ADC port
Read ADC at 10Hz with asynInt32 interface

---
asynRecord – register devices
Same asynRecord, change to DAC port
Write DAC with asynFloat64 interface

---
Tracing and Debugging
Tracing and Debugging
- Standard mechanism for printing diagnostic messages in device support and drivers
- Messages written using EPICS logging facility, can be sent to stdout, stderr, or to a file
- Device support and drivers call:
  - asynPrint(pasynUser, reason, format, ...)
  - asynPrintIO(pasynUser, reason, buffer, len, format, ...)
  - Reason:
    - ASYN_TRACE_ERROR
    - ASYN_TRACEIO_DEVICE
    - ASYN_TRACEIO_FILTER
    - ASYN_TRACEIO_DRIVER
    - ASYN_TRACE_FLOW
    - ASYN_TRACE_WARNING
- Tracing is enabled/disabled for (port/addr)
- Trace messages can be turned on/off from iocsh, vxWorks shell, and from CA clients such as EDM via asynRecord
- asynOctet I/O from shell

---
Recommended source file arrangement
Typical source file arrangement
Instrument support is placed in
    .../modules/instrument/<instrumentname>/Rx.y/
Each <instrumentname>/Rx.y/ directory contains at least
    Makefile
    configure/
    <InstrumentName>Sup/
    documentation/
    License

---
There’s a script to make this a little easier
Script to make this a little easier
- mkdir /…/modules/instrument/myinst/head
- cd /…/modules/instrument/myinst/head
- /<path to ASYN support mopdule>/bin/<arch>/makeSupport.pl
          -t streamSCPI myinst
  Makefile
  configure/...
  myinstSup/
    Makefile devmyinst.db devmyinst.proto
  documentation/
  devmyinst.html
- A few changes to the latter 3 files and you’re done!
- Notice that there are no C or C++ files.
  - Running make just copies the .db and .proto files to the support module top-level db/ directory.
[Speaker Notes: Merely modify the latter three files and your instrument support is done!]

---
Introduction to Stream Device
- Generic EPICS device support for devices with “byte stream” communication.
  - RS-232 (Local serial port or LAN/Serial adapter)
  - TCP/IP
  - VXI-11
  - GPIB (Local interface or LAN/GPIB adapter)
  - USB-TMC (Test and Measurement Class)
- A single stream device module can serve to communicate using any of the above communication mechanisms.
[Speaker Notes: Merely modify the latter three files and your instrument support is done!]

---
Introduction to Stream Device
- Command/reply messages:
  - *IDN?
  - SET:VOLT 1.2
  - Non-ASCII ‘strings’ too
- Command generation and reply parsing configured by protocols
- Formatting and interpretation handled with format converters
  - Similar to C printf/scanf format strings
  - Custom converters too, but not easy
[Speaker Notes: Merely modify the latter three files and your instrument support is done!]

---
Stream Device Protocols
- Defined in protocol files
- Plain ASCII text file
- No compiling – IOC reads and interprets protocol file(s) at startup
- Protocols are linear
  - No looping
  - No conditionals
  - Rudimentary exception handlers
- A single entry can read/write multiple fields in one or many records
- Output records can be initialized from instrument at IOC startup
  - With one big caveat – instrument must be on and communicating at IOC startup
[Speaker Notes: Merely modify the latter three files and your instrument support is done!]

---
StreamDevice EPICS Database
record(bo, "$(P)$(R)CLS") {
    field(DESC, "SCPI Clear status")
    field(DTYP, "stream")
    field(OUT, "@devmyInst.proto cmd(*CLS) $(PORT) $(A)")
}
record(longin, "$(P)$(R)GetSTB") {
    field(DESC, "SCPI get status byte")
    field(DTYP, "stream")
    field(INP, "@devmyInst.proto getD(*STB) $(PORT) $(A)")
}
DTYP=stream
INP/OUT fields specify protocol file name, protocol entry (with optional arguments), ASYN port and address.
Address can be any value (typically 0) for single-address interfaces.

---
StreamDevice Protocol File
cmd {
    out "\$1";
}
getD {
    out "\$1?";
    in "%d";
}
Protocol entries contain statements to produce output and request input
C-style escape sequence can be used ('\r', '\n', '\033', '\e')
Format converters are similar to those used by C printf/scanf
By default the VAL or RVAL field is used as the data source/destination
Can refer to any field, even in another record

---
StreamDevice Additional Records
DTYP ≠ stream for protocol entry additional records:
record(stringin, "$(P)$(R)Serial")
{
    field(DESC, "Serial number")
    field(DTYP, "Soft Channel")
}
record(ai, "$(P)$(R)VP5")
{
    field(DESC, "+5V supply")
    field(DTYP, "Raw Soft Channel")
    field(EGU, "V")
    field(PREC, "3")
    field(LINR, "SLOPE")
    field(ESLO, "1e-3")
…
record(longin, "$(P)$(R)Temp1")
{
    field(DESC, "Sensor 1 temperature")
    field(DTYP, "Soft Channel")

---
StreamDevice Protocol File
Protocol entries can be long – Use multiple lines and string concatentation to improve readability
query {
    out "Q";
    in ":"
       "SN=%(\$1Serial.VAL)39[^,],"
       "UN=%(\$1Name.VAL)39[^,],"
       "IP=%*[^,],"
       "V3=%d,"
       "V5=%(\$1VP5.RVAL)d,"
       "V+12=%(\$1VP12.RVAL)d,"
       "V-12=%(\$1VM12.RVAL)d,"
       "T1=%(\$1Temp1.VAL)d,"
       …
       "POH=%(\$1HoursOn.VAL)g,"
       "MAXTMP=%(\$1MaxTemp.VAL)g;"
}
Notice the use of the width field – guard against buffer overruns!

---
StreamDevice Protocol File – Terminators
Terminators can be set globally or per entry.
Some interfaces can handle only a single character. If device replies with '\r\n' then specify InTerminator='\n' and ignore the '\r' in the reply.
InTerminator = "\n";
OutTerminator = "\r";

---
StreamDevice Protocol File – Initial Readback
Useful to set initial value of output records to match the value presently in the instrument.
@init ‘exception handler’
Often the same as the corresponding readback prototype entry
getF {
    out "\$1?";
    in "%f";
}
setF {
    @init { out "\$1?"; in "%f"; }
    out "\$1 %f";
}
record(ao, "$(P)$(R)IntegrationTime")
{
    field(DESC,"Reading integration time")
    field(DTYP,"stream")
    field(OUT, "@devKeithley6487.proto setF(NPLC) $(PORT) $(A)")

---
Adding StreamDevice/ASYN instrument support to an application
- This is easy because the instrument support developers always follow all the guidelines – right?
- Most of these steps apply to pretty much any support module, not just StreamDevice/ASYN instruments.

---
Make some changes to configure/RELEASE
Make some changes to configure/RELEASE
- Edit the configure/RELEASE file created by makeBaseApp.pl
- Confirm that the EPICS_BASE path is correct
- Add entries for the instruments and ASYN:
DAWN_RUSH =/usr/local/epics/R3.14.12/modules/instrument/DawnRuSH/R1-0
ASYN =/usr/local/epics/R3.14.12/modules/soft/asyn/asynR4-21
EPICS_BASE=/home/EPICS/base

---
Modify the application Makefile
  ⁝
  xxx_DBD += base.dbd
  xxx_DBD += stream.dbd
  xxx_DBD += drvAsynIPPort.dbd
  (and/or drvAsynSerialPort.dbd, drvAsynUSBTMC.dbd, etc.)
  - xxx_DBD += asyn.dbd
  - ⁝
  - xxx_LIBS += stream asyn

---
Modify the application database Makefile
1. Copy the instrument support database and prototype files to the application <top>/db/ directory:
  ⁝
  DB_INSTALLS += $(DAWN_RUSH)/db/devDawnRuSH.db
  DB_INSTALLS += $(DAWN_RUSH)/db/devDawnRuSH.proto

---
Modify the application startup script
Modify the application startup script
epicsEnvSet("CRATE_ADDRESS","$(CRATE_ADDRESS=crateapex01:23)")
    (above line is optional, but makes it easy to override for testing)
epicsEnvSet("STREAM_PROTOCOL_PATH","${TOP}/db")
⁝
drvAsynIPPortConfigure("CR0","$(CRATE_ADDRESS) TCP",0,0,0)
⁝
dbLoadRecords("db/devDawnRuSH.db","P=apexCrate:,R=1:,PORT=CR0")
- P,R	– PV name prefixes – PV names are $(P)$(R)name
- PORT	– ASYN port name from corresponding devxxxConfigure command

---
Lab Session
Control ‘network-attached device’
- Host www.xxx.yyy.zzz – TCP Port 24742
- '\n' command terminator, '\r\n' reply terminator
- *IDN?
  - Returns device identification string (up to 100 characters)
LOAD?
  - Returns three floating-point numbers separated by spaces (1, 5, 15 minute load average)
ON?
  - Returns OFF/ON (0/1) status
- VOLTS?
  - Returns most recent voltage setting
- CURR?
  - Returns current readback (±11A)

---
Lab session – Control ‘network-attached device’
Lab Session
Control ‘network-attached device’
ON [0, 1]
  - Turns supply OFF/ON (0/1)
VOLTS x.xxxx
  - Sets voltage (±10V range)