## Slide 1: Status of the European Spallation Source
Timo Korhonen
Chief Engineer, Integrated Control System Division
www.europeanspallationsource.se
October 21, 2014

## Slide 2: The European Spallation Source
An accelerator-based neutron source to be built in Lund, southern Sweden
  Material and life sciences research
A collaboration of 17 European nations
  Construction budget about 1860 million Euro
Targeted to be the world’s most powerful neutron source
  5 MW beam power, 2.5 GeV proton energy, 14 Hz repetition rate, 2.86 ms pulse@50 mA beam current
  Superconducting linac, rotating tungsten target
  22 neutron beam lines in construction budget

## Slide 3: The European Spallation Source
First protons planned by 2019
Project completion by 2025
  Full beam power, 22 neutron beam lines
Accelerator in Lund,Sweden and data processing center in Copenhagen, Denmark

## Slide 4: Machine layout
(200 m)

## Slide 5: Target and the neutron beam lines
Rotating wheel target – beam has to hit in the middle of the sector.

## Slide 6: Office and experiment areas – nice…

## Slide 7: ESS construction has started!
ESS is funded
and
Construction is underway!
This aerial photo has been taken about two weeks ago.

## Slide 8: ESS Control System
ESS Integrated Control System Division (ICS) is in charge of building the control system(s) for the accelerator, the neutron target, and providing controls for the beamline components (in cooperation with the colleagues from science directorate)
Project scope includes also
  Conventional facilities control integration
  protection systems (Machine, Personnel)
  Global timing system for site-wide synchronization
Some parts of the controls will be provided by ESS partner laboratories as in-kind contributions
  e.g., proton source and LEBT controls by Saclay (France)

## Slide 9: Some technology decisions
Using EPICS for controls in the whole facility
  From accelerator to neutron beamlines
  Plan to benefit from EPICS version 4 facilities
    pvAccess as the binding communicating layer
    Services (e.g. physics model as a service) for the accelerator
Participating in the DISCS (Distributed Services for Controls) collaboration
  Databases and applications for facility and device configuration data
  Middle-layer services (see http://openepics.sourceforge.net/)
CS-Studio as the generic user interface tool
  Control room, subsystem developers, etc.
Committed to work together with the EPICS community
  Combining our resources we can make more and better things

## Slide 10: Technology decisions cont.
Using MRF event system for global timing
  Synchronization in the whole facility
  Timing supports beam synchronous applications (in discussion with PSI about co-development)
  Looking at future developments together with some new projects (ELI-Beams, SwissFEL, others)
Machine protection is of prime importance
  Ability to switch off beam mid-pulse (10 us time range)
    FPGA-based fast interlock
    Slow devices connected to PLC-based system
  Has to be synchronized with beam operation
    Ramping up with beam intensity, pulse length and repetition rate

## Slide 11: Controls hardware decisions
Defining hardware standards – for the whole spectrum
  Standardize on one PLC brand – as far as we can
    To reduce complexity
  Digital platform form factor
    One form factor should cover the segment of fast signal processing
      Mainly beam diagnostics and LLRF
    Going towards MTCA.4 – carefully, though
      Still a new standard with compatibility, etc., issues
    Setting up collaborations for a full framework
      FMC standards, development framework for the whole cycle (HW&FW&SW)
  Plan to use EtherCAT for middle range between PLCs and MTCA
    pulse-synchronized operations, distributed, kHz range acquisition

## Slide 12: Controls platforms
Evaluating motion controller platforms
  Current designs based on DeltaTau GeoBrick
  Working together with colleagues from science directorate
Controls network design starting
    a network and servers expert hired recently
    Server hall (Lund site) design ongoing
Starting to look at virtualization solutions
  “soft” IOC deployment, development servers
Collaborative tools in heavy use
  Atlassian toolkit: JIRA (bugtracker), Confluence (Wiki, web tool) and BitBucket (repository/Git management)

## Slide 13: Common services
Configuration databases and related tools
  (Controls) configuration, cabling, naming service, access control (RBAC) etc.
IOC development workflow and tools
  Still searching for optimal development and deployment flow
    How to deploy 600+ IOCs in a short time?
    How to manage these after deployment?
    How to support our off-site partners>
  “IOC Factory” – you will hear about that in the future
Use tools from the community whenever possible
  CS-Studio, Archiver, Save&Restore, alarm handler
  Contribute to development when appropriate
Use resources to develop things that do not exist
  Our local infrastructure, for example…

## Slide 14: Summary
ESS construction has started
  New accelerator, new institute, new…everything
  Roll up the sleeves and start building systems
Control system effort is ramping up
  Moving from prototyping to design decisions
  Hiring people (watch our web pages!)
  Working in collaborations and with in-kind contributors in member states (still looking for partners)
Lots of things to build
  Many challenges, many opportunities