## Slide 1: ITER Fast controller EPICS support
Vishnu Patel
ITER Organization
Control System Division

## Slide 2: Content
Introduction
Software Architecture
PXI-6259
Timing Board
PXIe-6368
PXI-6528
Conclusion
Content

## Slide 3: Goal for ITER CODAC (Control, Data Access and Communication)
Ensure all ITER Plant Systems Instrumentation & Control are designed, implemented and integrated such that ITER can be operated as a fully integrated and automated system.
Higher reliability and availability.

## Slide 4
Physical Architecture

## Slide 5
What constitutes a fast controller?
Industrial computer
I/O chassis as required
Interlinked with a PCI Express bus extension
In an I&C cubicle

## Slide 6
What constitutes a fast controller?
The industrial computer
I/O chassis (a PXIe rack)
TCN timing card NI PXI-6683H
A/D I/O card NI PXI-6259
Signal terminal block
(patch panel)

## Slide 7: Standard I/O Boards
N.I. PXI-6682/PXI-6683H : Synchronization and timing (IEEE1588-2008 / TCN)
  N.I. PXI-6259: multi-function data acquisition
    16bits analog input channels (16 Diff. /32 Single Ended) (1.25MS/s)
    16bits analog output channels (4) (2.86 MS/s)
    Digital input/output channels (48)
  N.I. PXIe-6368: High Performance multi-function data acquisition
    16bits analog input channels (16 Diff.) (Simultaneous, 2MS/s)
    16bits analog output channels (4) (3.3 MS/s)
    Digital input/output channels (48)
  N.I. PXI-6528 : Digital I/O
    24 optically isolated input channels
    24 solid-state relay output channels
  N.I. PXIe-7961R : FlexRIO
    Virtex-5 SX50T, 8160 FPGA Slices, 16 DMA Channels
  N.I. PXIe-7966R : FlexRIO
    Virtex-5 SX95T , 14720 FPGA Slices, 512MB DRAM, 16 DMA Channels 8160
    The Supported boards are listed in the ITER Catalog of I&C products - Fast Controllers (345X28).

## Slide 8: Software Architecture

## Slide 9
The main challenge for CODAC is INTEGRATION
CODAC Core System
Operation Applications

## Slide 10
PLC
PLC IOC
PSH IOC
PSH
CODAC Terminal
Operator Interface (OPI)
Alarm views
Data plots
Control System Studio HMIs
Alarm server
Archive Server
CODAC
CODAC Server
Alarm handling
Archiving
PSH:
I&C monitoring
PLCs Gateway
I&C coordination
Fast Controller:
I/O interface
HPN interfaces: TCN, SDN, DAN
RT control
PCF
IOC
I/O
Fast Controller
SDN
TCN
DAN
RT task
PON / CA
CODAC Core System (CCS)

## Slide 11: The Operating System(RHEL) & EPICS in CCS
ITER selected Red Hat Enterprise Linux for the x86-64 architecture (RHEL x86_64) & open source control system EPICS
  CCS 4.3 -> RHEL 6.3 -> EPICS 3.14 , asynDriver 4.21
  CCS 5.0 -> RHEL 6.5 -> EPICS 3.15 , asynDriver 4.23 (Feb 2015)
For fast feedback control a real-time enabled version of RHEL, RHEL MRG-R, is deployed.
  Optimized kernel for real-time applications
  More deterministic latencies / reduced jitter

## Slide 12: Standard Software Support
CODAC Core System includes the software for ITER standard I/O boards
  Linux driver
  EPICS integration (EPICS device support)
  SDD integration (configuration via SDD tools)

## Slide 13: Self-Description Data Definition (SDD) Editor

## Slide 14: EPICS device support
  Basic EPICS Device Driver
  . PXI-6259: multi-function data acquisition.
asynDriver based Device Driver
PXI-6682 & PXI-6683h : Synchronization and timing.
  PXIe-6368: High Performance multi-function data acquisition.
  PXI-6528 : Digital I/O.
Future device Support
  FlexRIO boards (PXIe-7961R/PXIe-7966R ).
  cRIO.

## Slide 15: PXI 6259 DAQ Board

## Slide 16: PXI 6259 DAQ Board
AI Channels
Channel : 32 Single-Ended Channels
/16 Differential Channels
Sample rate : 1.25Ms/s single channels
1Ms/s multi channels (all)
AO Channels
Channel : 4
Update rate :
  1.25Ms/s per each channel (4 Ch)
  2.86MS/s (1 Ch)
Digital I/O
Bidirectional Channel : 48

## Slide 17: PXI 6259 Board functions
General
  Device Information
  Software version
DAQ mode Support
  Software timed acquisition
  Hardware timed acquisition
    Finite sample mode
    Continuous mode
Clock Settings
  Sampling rate
  Clock Source
  Clock divider
Triggering
  Set trigger
    Software
    Hardware (Start, Stop & Pause Trigger)
  Pre & Post samples

## Slide 18: PXI 6259 Board functions
DIO configuration
Analog Output configuration.
General purpose counter
Signal routing

## Slide 19: PXI 6259 Templates
Board level EPICS Template
  EPICS PV Prefix :- $(CBS1)-$(CBS2)-HWCF:6259-$(BOARDTYPEIDX)-
Channel level EPICS Template.
    EPICS PV Prefix :- $(CBS1)-$(CBS2)-HWCF:6259-$(BOARDTYPEIDX)-AI$(CHIDX)-
Function | PV Suffix | Record type | Description
num_samples | NS | longout | Set Number of sample to read
sample_rate | SR | longout | Set sampling rate of AI
BoardStatus | BS | mbbi | Read Board status
switch_acquisition | ACQ | bo | Start/Stop data acquisition
daq_mode | MODE | bo | Set Continuous or Finite AI acquisition mode
pretrig_samples | PRET | longout | Set Pre-trigger sample for AI acquisition
posttrig_samples | POST | longout | Set Post-trigger sample for AI acquisition
ai_conf | CONF | bo | Load/Reset AI configuration
Function | PV Suffix | Record type | Description
samples_read | SR | longin | Read Analog input of selected channel
channel_type | CT | mbbo | Set Channel Type (NRSE/RSE/DIFFERENTIAL

## Slide 20: Timing Boards (PXI-6682 & PXI-6683H)

## Slide 21: Timing Boards Functions
Receive ITER time
Synchronization of system time with Board time
Generate Future time events, Pulse and Clocks
  Front panel connector
  PXI backplane lines
  Synchronized event generation
Signal routing
Clock routing
Accurate Time-stamping of event
  External events (Front panel
  connector & Backplane lines)
Pulse sequence Programming on
the selected terminal.

## Slide 22: Timing Boards Templates
Board templates are
  nisync_clock_route.template -> 6 PVs
  nisync_device_info.template -> 15PVs
Terminal Templates are
  nisync_terminal.template -> 44 PVs
  nisync_timing_program.template -> 4PVs
Function | PV Suffix | Record type | Description
getTime | BDTM | waveform | Read Board time in second, nanosecond
getTime | HBDTM | stringin | Read Board time in Human readable format
deviceName | DEVNAME | stringin | Get device name
driverVersion | DRIVER | stringin | Get Linux driver version
abortAllFtes | FTEAALL | bo | Aboard all pending FTES
maxScheduledFtes | FTRMAX | Longin | Read Maximum number of scheduled Ftes
numPendingFtes | FTENUM | Loingin | Read number of pending FTEs
checkFteLevels | LVL_ERRS | longin | Check FTE level sequence error
deviceSerialNumber | SERIAL | loingin | Get device serial number
deviceStatus | STAT | mbbi | Get device status
syncStatus | SYNC | mbbi | Get device synchronization status
resetCard | RESET | bo | Reset the Device
Function | PV Suffix | Record type | Description
clockSource | BKPCMON | mbbi | Read Backplane clock source
clockSource | BKPSRC | mbbo | Connect the selected source clock to the Backplane clock
clockSource | CLKOMON | mbbi | Read Clock-out clock source
clockSource | CLKOSRC | mbbo | Connect the selected source clock to the to the Clock-out
clockSource | TMKCMON | mbbi | Read Time keeper clock source
clockSource | TMCSRC | mbbo | Connect the selected source clock to the to the Time keeper clock
  Device Information
    EPICS PV Prefix :- $(CBS1)-$(CBS2)-HWCF:$(SHORTBOARDTYPE)-$(BOARDTYPEIDX)-
  Clock Routing
    EPICS PV Prefix :- $(CBS1)-$(CBS2)-HWCF:$(SHORTBOARDTYPE)-$(BOARDTYPEIDX)-

## Slide 23: Timing Boards Templates
  Device Terminals
    EPICS PV Prefix :- $(CBS1)-$(CBS2)-HWCF:$(SHORTBOARDTYPE)-$(BOARDTYPEIDX)T$(CHIDX)-
Function | PV Suffix | Record type | Description
fteEnable | FTEE | bo | Enable or disable future time event
fteStatus | FTEM | bi | Returns whether future time event is enabled
fteTimeSec | FTES | ao | Set second part of the FTE time
fteTimeNsec | FTEN | longout | Set nano second part of the FTE time
fteLevel | FTEL | bo | Set level of future time event
fteGenerate | FTE | bo | Generate FTE with configured time
fteAbort | FTEA | bo | Abort FTE for configured time
    Future Time Event Records
    Timestamp Records
Function | PV Suffix | Record type | Description
timestampControlEdge | TSCG | mbbo | Set detection edge
timestampControlDecCount | TSDC | longout | Sets the decimation count for timestamping
timestampControlEnable | TSEN | bo | Enable or Disable timestamping
timestampRead | TS | waveform | Timestamp is read with 3 element waveform (second, nano-second, edge)
timestampStatusEnable | TSM | bi | Returns whether timestamping is enabled
timestampStatusEdge | TSMG | mbbi | Returns detection edge for timestamping
timestampStatusDecCount | TSMDC | longin | Returns decimation count for timestamps
    Pulse Generation Records
Function | PV Suffix | Record type | Description
pulseEnable | PLUSEE | bo | Enable or disable pulse generation
pulseStatus | PLUSEM | bi | Returns whether pulse is enabled
pulseTimeSec | PULSES | ao | Set second part of the pulse time
pulseTimeNsec | PULSEN | longout | Set nano second part of the pulse time
pulseWidth | PULSEW | ao | Set pulse width
pulseInvert | PULSEI | bo | Set pulse inversion
pulseGenerate | PULSE | bo | Generate PULSE with configured time
    Clock Generation Records
Function | PV Suffix | Record type | Description
clockEnable | CLOCKE | bo | Enable or disable clock generation
clockStatus | CLOCKM | bi | Returns whether clock is enabled
clockStartSec | CLOCKSS | ao | Set second part of the clock start time
clockStartNsec | CLOCKSN | longout | Set nano second part of the clock start time
clockEndSec | CLOCKES | ao | Set second part of the clock end time
clockEndNsec | CLOCKEN | longout | Set nano second part of the clock end time
clockPeriod | CLOCKP | ao | Set Clock period
clockDuty | CLOCKD | ao | Set Clock duty cycle
clockGenerate | CLOCK | bo | Generate clock with configured time

## Slide 24: Timing Boards Templates
  Device Terminals
    EPICS PV Prefix :- $(CBS1)-$(CBS2)-HWCF:$(SHORTBOARDTYPE)-$(BOARDTYPEIDX)T$(CHIDX)-
Function | PV Suffix | Record type | Description
fteEnable | FTEE | bo | Enable or disable future time event
fteStatus | FTEM | bi | Returns whether future time event is enabled
fteTimeSec | FTES | ao | Set second part of the FTE time
fteTimeNsec | FTEN | longout | Set nano second part of the FTE time
fteLevel | FTEL | bo | Set level of future time event
fteGenerate | FTE | bo | Generate FTE with configured time
fteAbort | FTEA | bo | Abort FTE for configured time
    Future Time Event Records
    Timestamp Records
Function | PV Suffix | Record type | Description
timestampControlEdge | TSCG | mbbo | Set detection edge
timestampControlDecCount | TSDC | longout | Sets the decimation count for timestamping
timestampControlEnable | TSEN | bo | Enable or Disable timestamping
timestampRead | TS | waveform | Timestamp is read with 3 element waveform (second, nano-second, edge)
timestampStatusEnable | TSM | bi | Returns whether timestamping is enabled
timestampStatusEdge | TSMG | mbbi | Returns detection edge for timestamping
timestampStatusDecCount | TSMDC | longin | Returns decimation count for timestamps
    Pulse Generation Records
Function | PV Suffix | Record type | Description
pulseEnable | PLUSEE | bo | Enable or disable pulse generation
pulseStatus | PLUSEM | bi | Returns whether pulse is enabled
pulseTimeSec | PULSES | ao | Set second part of the pulse time
pulseTimeNsec | PULSEN | longout | Set nano second part of the pulse time
pulseWidth | PULSEW | ao | Set pulse width
pulseInvert | PULSEI | bo | Set pulse inversion
pulseGenerate | PULSE | bo | Generate PULSE with configured time
    Clock Generation Records
Function | PV Suffix | Record type | Description
clockEnable | CLOCKE | bo | Enable or disable clock generation
clockStatus | CLOCKM | bi | Returns whether clock is enabled
clockStartSec | CLOCKSS | ao | Set second part of the clock start time
clockStartNsec | CLOCKSN | longout | Set nano second part of the clock start time
clockEndSec | CLOCKES | ao | Set second part of the clock end time
clockEndNsec | CLOCKEN | longout | Set nano second part of the clock end time
clockPeriod | CLOCKP | ao | Set Clock period
clockDuty | CLOCKD | ao | Set Clock duty cycle
clockGenerate | CLOCK | bo | Generate clock with configured time

## Slide 25: EPICS interface for pulse time
One timing is defined by the following PVs:
Control of the time origin (suffix: “-O”), expressed as a double and representing an absolute time in seconds.
Control of the time offset from the origin , called delay (suffix: “-D”), expressed as a double and representing a time in seconds with the resolution of a nano-second and with an absolute limit of one day.
Control of the terminal line level (suffix: “-L”) to High or Low.
An enable/disable flag (suffix: “-E”) for adding/removing the timing to the list of FTEs.

## Slide 26: PXIe-6368 DAQ Board

## Slide 27: PXIe-6368 DAQ Board
16 simultaneous analog inputs at 2MS/s/ch , 32MS/s total AI throughput (16 bit resolution)
Four analog outputs, 3.33 MS/s (16 bit resolution)
48 digital I/O lines
  32 hardware-timed up to 10MHz
  16 PFI
Four 32 bit counters
Analog and digital triggering
Acquisition mode.
  Continuous
  Finite sample
  Reference triggered

## Slide 28: PXIe-6368 DAQ Board Function
All the Functions for PXI-6259
Retriggerable acquisition mode
Board level and Channel level EPICS Template.
waveform and ai record support for Analog input.
DIO configuration with EPICS PVs.
Analog Output configuration with EPICS PVs.

## Slide 29: PXIe 6368 Templates
Board level EPICS Template
  EPICS PV Prefix :- $(CBS1)-$(CBS2)-HWCF:6368-$(BOARDTYPEIDX)-
Channel level EPICS Template.
    EPICS PV Prefix :- $(CBS1)-$(CBS2)-HWCF:6368-$(BOARDTYPEIDX)-AI$(CHIDX)-
Function | PV Suffix | Record type | Description
change_ai_mode | CHAIMO | mbbo | Change the AI acquisition mode
reset_load_ai | LDAICF | bo | Load/Reset AI configuration
no_of_samples | AISMPL | longout | Number of AI sample to be acquire
pulse_ai | AIPU | mbbo | Generate Software pulse for AI
sampling_rate_ai | AISR | longout | Set AI sampling rate
start_stop_ai | AISTSP | bo | Start/Stop Analog acquisition
timebase_ai | AITB | longout | Set AI timebase source
Function | PV Suffix | Record type | Description
Read_ai | AIW$(CHIDX) | waveform | Read AI samples of channel $(CHIDX)

## Slide 30: PXI-6528 DIO Board

## Slide 31: PXI-6528 DIO Board Functions
Read Device information
Bit and Byte write/read on hardware port (3 input and 3 output ports)
Signal routine.
Watchdog configuration
Level change on watchdog
Level change detection
Input port filter
Output port Power up state
driver
interface
client / asynUser
Byte
bus controller (port)
Bit

## Slide 32: PXI-6528 Templates
  EPICS PV Prefix :- $(CBS1)-$(CBS2)-HWCF:6528-$(BOARDTYPEIDX)-
Function | PV Suffix | Record type | Description
noboard | BS | bi | Give board presence
setfilterinterval | FILTINT | longout | Configure the internal filter interval
setrtsiinputroute | RTSIINPROUT | longout | Select the RTSI input port lines
setrtsioutputroute | RTSIOUTROUT | longout | Select the RTSI Output port lines
setrtsiwatchdogtrigger | RTSIWDGTRIG | longout | Configure an RTSI line to act as a hardware trigger for the watchdog timer.
setwatchdogtimeout | WDGTOUT | ao | Set watchdog timeout
setportpowerup | POWERP3 | longout | Set port3 power up state
setportpowerup | POWERP4 | longout | Set port4 power up state
setportpowerup | POWERP5 | longout | Set port5 power up state

## Slide 33: Management Tools
Tool | Scope | Reference
Subversion | Software source code evolution | https://svnpub.iter.org/codac
Bugzilla | Issue tracker | https://bugzilla.iter.org/codac
Central SDD | I&C production projects | https://sdd.iter.org
CLM | Inventory control | https://psp.iter.org/PsProfile/page/inventory/

## Slide 34
Conclusion
Developments and distribution of EPICS Device Drivers are stable.
  PXI-6259
  Timing Boards (PXI-6682 & PXI-6683H
  PXI-6528
ALL of the requirement for PXI-6259, Timing boards (PXI-6682 & PXI-6683H) and PXI-6528 are completed
PXIe-6368 EPICS device Driver is under progress.
More efforts will be applied in improvement.
Thank you