LOCKOUT/TAGOUT PROCEDURE AND CHECKLIST

For construction and service contractors, when the 110/208V T (technical panels ONLY must be locked out, an authorized FMS employee, AES-CFG employee or Floor Coordinator must apply the first lock.

- Prerequisites

1.  Full knowledge of ES&H Manual Section 7.1, Control of Hazardous Energy and Lockout/Tagout.

2.  Training is up to date. Required Courses are:  ESH114, ESH”114PR, ESH371, and ESH75 (NFPA 70E).

3.   Full knowledge of equipment or system to be shut down.

4.   Authorization by division management to perform lockout/tagout.

- To initiate lockout/tagout, follow the procedure below. Check off steps as they are completed.

1.  The Floor Coordinator or AES-CFG employee must identify all energy sources and disconnect switches, valves, or other energy-isolating devices that control the supply of energy to the equipment to be locked out. If there is more than one source of energy, a complex equipment specific procedure is required. The type and magnitude of energy and associated hazards must be identified. Refer to up-to-date diagrams, schematics, labeling, and drawings as appropriate to identify these energy sources and hazards.   The Floor Coordinator will not do a complex lockout.  The complex lockout with be referred to AES-CFG.

2.  The Floor Coordinator or AES-CFG employee must notify the affected employees about power to be shut off, work in progress and/or work to begin under lockout/tagout; this notification can be verbal.

3. If the equipment is operating, an employee who is qualified for the equipment under normal

operating conditions must shut it down following standard procedures and ensure that controls are returned to the “OFF” position.

******NOTE:  Steps 1 – 3 must be performed by The FC or AES-CFG employee before calling FMS if FMS is going to perform the lock out. ********

4.  The Floor Coordinators, AES-CFG or FMS must disengage all energy sources to the equipment

using energy-isolating devices and supply facility lockout of a circuit that a construction or service contractor will be working on.  The facility lockout is applied first.

5.  Each ANL employee who is to work on the equipment must place a lock on the energy-isolating devices with approved locks obtained from the nearest lockout station or from the FMS lockout station.   Each lock removed from the station must be registered in the station log book.  Construction and Service contractors must supply their own locks which can not be a Master red banded lock.  Multiple lock tongs will be used when more than one individual is working on the deenergized system. A danger lockout tag must accompany each lock and indicate the identity of the employee(s) applying the locks and the date applied. The individual who applies a lock on a lockout device must control the key to that lock until the lock is removed. Attempt to operate the device/disconnect(s) to verify that the lock(s) prevents its operation.

6.  All stored energy must be dissipated where possible or restrained by blanking, grounding, etc. Prior to starting work on the equipment that has been locked out, the employees who are to work on the equipment must collectively verify that it is isolated and deenergized. This can be accomplished by testing start/stop controls and/or by visual inspection of energy-isolating devices (e.g., blades, blanks). When a possibility of direct exposure to electrical components or wiring exists when performing the work, an NRTL-listed voltage tester or multimeter meeting the requirements of Section 7.1.19 must be used by a qualified electrical worker to test each phase-to-phase and phase-to-ground combination to ensure the electrical energy is off (zero electrical energy verification). Proper PPE per NFPA 70E must be worn when conducting this step as if the electrical power were on. The three-point testing methodology must be used: test instrument, test circuit, retest instrument. Caution: Auto-start switches must be reset to neutral or off position after the test. When required, ground the electrical system to eliminate induced voltage and/or to ensure dissipation of stored energy.

4.  NOTE:  The equipment is now locked and tagged, and ready to be worked on.

- Release from Lockout/Tagout

1.  When work is complete, ensure that all controls are returned to “OFF,” all tools are removed, and all personnel are clear of the equipment before start of unlocking procedures. Remove any grounding that was applied.

2.  Notify the affected employees that power will be restored.

3.  The locks and tags must be removed by the individuals who installed them.

4.  Restore power and place the machine or system back into service.

5.  Locks must be returned to the lockout station and the logbook entry completed.